IEC 61850 Interoperability Testing
Oct 2019

Charlotte, NC USA

General Integrated Application Test Cases

1	Philosophy (new)	6

1.1	Engineering Configuration	9

1.2	Networking	11

1.3	Security	12

1.4	Time Synchronization	12

1.5	Process Bus	13

1.6	Substation Maintenance (disruptive)	13

2	Normal Testing	13

2.1	SCL	13

2.2	Client/Server	15

2.3	GOOSE	38

2.4	Sampled Values	40

3	Substation Maintenance	49

3.1	Change SCD Communication Configuration: DIS-SCL-01	49

3.2	IED Addition to Bay	49

3.3	IED Replacement	54

4	PTP	56

4.1	Process bus clock failure Test Cases	56

5	IED Isolation Testing	57

5.1	Client/Server	58

5.2	GOOSE	62

5.3	Sampled Values	65

6	Disruptive Testing	67

6.1	GOOSE	67

6.2	Sampled Values	68

6.3	PTP	69

6.4	IED Failure/Power Down	76

6.5	EAP failure	88

6.6	Redundant Firewall	89

6.7	Firewall with no failsafe	90

7	Firewall/EAP and GOOSE Monitoring Testing	92

7.1	Use case: Intruder with different source MAC address and power-up	92

7.2	Use Case: Intruder with the same source MAC address and power-up	92

7.3	Use Case: Intruder with the same source MAC address and future StNum	93

8	Network Failure	93

8.1	Test case name: NET-FAIL-01	93

8.2	Test case name: NET-FAIL-02	94

9	Validation of device synchronization (used by most clock synchronization tests)	96

Introduction / History / Actions

Changes to document:

- Added SV redundancy use cases from SEL. See page 42.

Working backwards:

- SCD Engineering to start September 9 to be completed draft SCD by September 16th.

- Validated ICDs must be available on the 8th.

- Signal exchange  & Assignment of positions completed September 2.   Christoph Brunner, Jun, Dean will analyze.

- Participation Matrix – Completed by September 2.  Desired completion by August 26th.

  - Resurrect the address assignment sheet from 2017 and modify as needed – completed during PACWorld.

    - Vendors at 2017 IOP will be attempted to be given the same address space.

- Assignment of IEDs into SLD functions - who and when

2. To assist SCL Engineering, will ICT provide any of the following information in ICD as default based on Integrated Apps requirement (so that SCTs can focus on Signal mapping between IEDs) ?

a) Communication addressing (Subnetwork, IP, Subnet Mask, Gateway)

b) Report Configuration (ID, Dataset config, TrgOpts, OptFlds etc)

c) GOOSE Configuration (GOOSE ID, Dataset config, Multicast Address, VLAN ID, Priority etc.)

3. Will there be multiple configuration for same IED ? will there be more than one SCD with same IED placed at multiple locations in the SLD ?

SCL:

- Remote Substation for differential protection or line protection. Design work to use GOOSE.

- Low voltage of SLD will be one substation

- High voltage of SLD will be the other substation

- Control Center will be there.

- Jun will distribute 2017 SSD to group

- Need to discuss how to change SCD’s and disruptive tests.

Need to get with simulation companies to divide responsibilities.

Network decisions:

- Copper Ethernet – follow 2017 guidance

- Interconnection between intermediate systems (routers, switched): Gig

- All switches to support extended Ethernet frame (to allow PRP).

- Switches: 100MB or Gig (auto-negotiate)

- Switches and Coupler – PTP support

- Power is 120 AC.

- HSR wait for participation matrix…

- Redboxes – supplied by Siemens/RuggedCom

- Coupling between process bus and station bus – RuggedCom

- Routers: L2TP and PIM and DCSP.

- Addressing will be primarily IPv4.  IPv6 testing will be limited.

- Omicon will bring at least 1 Daneo.

- Need to determine how to synchronize grandmasters…

- Separate VLANs:

  - Station bus: High voltage 2, Low Voltage 3

  - Process bus: 4, 5, maybe more

# Philosophy (new)

The Single Line Diagram (SLD), shown in Figure 1, represents the High Level Design (HLD) template for the application to be used as the framework for testing.  Figure 2 depicts some of the intended signal and message exchanges that will be used.

Figure 1: HLD Single Line Diagram

Figure 2  Partial Single Line Diagram showing typical objects, devices and signals

The integrated application is intended to consist of two (2) substations and 1 control center.  This construct is to allow testing of information exchange/substation functions such as:

- Intra-substation application functions

  - Breaker and a half scheme

  - Breaker fail/reclose

  - Ring bus

- Inter-substation

  - Line differential protection or distance protection

- Substation to/from Control Center

  - Typical SCADA functions

In order to accomplish these functions, sampled values will be used to provide CT/PT information for the devices implementing the application functions.

There are two additional service capabilities that are to be utilized within the scope of the integrated application: security and time synchronization.

Figure 3:  Overview of Integrated Applications Services and Interfaces

Figure 3 depicts the different IEC 61850 levels showing the equipment that may be part of the integrated application and the communication services used to exchange information between the various levels.

New in 2019 is the ability to exchange synchrophasor information through the use of Routable Sampled Values (R-SV) from devices that have Phasor Measurement Unit (PMU) capability.  Many utilities deploy IEEE C37.118 for synchrophasors today, however these are not secured in a standard mechanism. There is an IEEE report D0.90 that specifies how to convert from C37.118  to R-SV and that type of conversion is shown as a Phasor Data Concentrator (PDC) in the figure.

The figure shows the various communication services  that are to be utilized in the in the integrated application and form the basis for the test cases in this document.  Additionally, there are test cases/considerations that need to address system engineering including device and network configuration.

The following subclauses provide a high level of the types of testing that are intended to be performed.

## Engineering Configuration

This set of tests are more offline than online tests and involve the substation configuration language.  The purpose is to validate that each implementation provides a valid IED Capability Description (ICD) file and that the System Configuration Tool (SCT) to/from IED Configuration Tool (ICT) exchanges are supported as defined in IEC 61850-6.

Figure 4: IEC 61850-6 Defined Exchanges

The use of System Specification Description (SSD) files and System Exchange Description (SED) files are out-of-scope of the integrated application testing and should be covered in the SCL testing area. The use of Configured IED Description (CID) files are for ICT to device exchange and are not required to be supported by an ICT.  Thus , the testing of CIDs is out-of-scope.

There are two types of tests that need to occur:  Initial configuration and configuration changes to operational systems.

Initial Configuration

These steps/tests are required in order to create an operational system:

- ICD validation – tests that the IED Capability Description (ICD) files provided by the vendors are valid.

- SCT to ICT Exchange – tests that the engineered solution can be exchanged to the IED Configuration Tool and that the tool can correctly configure the device based upon the System Configuration Description (SCD) file.  This test may cover:

  - Later binding of Inref and Blkrefs

  - Ability of SCT to generate an Edition 1 SCD.

- ICT to SCT exchange and IED Instantiation Description (IID) file in order to provide any changes that the ICT made in order to configure the device .

Changes to Operational Systems

These steps/tests are typical changes that may occur to an operational system:

- Addition of a new device into the operational system.

- Removal of a device from an operational system (disruptive).

## Networking

In order to stage an operational system, the communication network(s) must be designed, deployed, and tested.

Figure 5: High Level Routing Network Design

Figure 5 shows the communication requirements for the routers between the substations and control center.

- Protocol Independent Multicast (PIM) required to support R-GOOSE and R-SV

- Virtual Private Network (VPN) – The actual protocol to be utilized will be chosen during the network design activity.  The intent of the VPN is to provide encryption of packets as they are exchanged over the simulated wide are connections.

It is intended that the VPN provide the confidentiality protection for packets whereas the IEC 62351-6 security mechanisms will provide packet integrity and authentication. This separation is done so that the requirement of NERC edge packet inspection can be met.

The edge of each interface (e.g. Control Center->Substation and Substation<-> Substation) requires a firewall that can provide access control and potentially packet inspection capability.  The routers are responsible for supporting IGMPv3 and PIM in order to support R-GOOSE and R-SV.  The depending upon the positioning of the firewall (e.g. outward of the router or inside of the router) must not block the protocols required for use inside the perimeters.

The switches provided in the substations shall support Precision Time Protocol, IGMP snooping, extended Ethernet frame size (required to support PRP),  and shall be configured with a single mirror port.

Network resiliency, within the substation(s), shall be provided through the use of PRP or HSR.

The test cases for PRP, or HSR, connected Dual Attached Network (DAN) device need to include the following:

- Normal operation

- Failure of a single connection

- Failure of both connections (disruptive)

For PRP an additional test for DANs shall be added:

- Single switch failure

In order for this test to be non-disruptive, the switch that is failed must not have a Single Attached Node (SAN) connected to it.

## Security

The intent of security testing is to test IEC 62351-6 and network security based upon NERC expectations.  The actual test cases will be detailed in a specific section not within the integrated application testing document.

- For Client/Server:

  - The support of integrity only TLS cypher suites to facilitate edge packet inspection

  - The support of encrypting  TLS cypher suites to facilitate end-to-end confidentiality.

  - The support of strong Authentication at the application level.

- For R-GOOSE/R-SV:

  - The support of integrity only to facilitate edge packet inspection

  - The support of encryption to facilitate end-to-end confidentiality.

- Key and certificate management:

  - Key management for R-GOOSE and R-SV.

  - Certificate management including but not limited to:

    - Certificate expiration

    - Certificate revocation

    - Certificate Authority chaining

It is also intended to stage other non-IEC 61850 required security services (in the control center) consisting of Radius and Syslog.

## Time Synchronization

Two types of time services are intended to be provided as part of the integrated application: SNTP and PTP protocols of IEC 61850-9-3/IEEE c37.238.

For PTP, there shall be multiple grand masters within the substations.

- Operational – Do devices all pick the same best master.

- Fail the selected grandmaster and check that the devices select the same best master (disruptive).

- Fail all grandmasters and observe behavior (disruptive).

  - For sampled value publishers, observe hold over time

  - For sampled value subscribers, observe behavior when holdover time expires.

- Power-up a single grandmaster and observe the behavior (time jump or ramp) of the devices.

## Process Bus

It is intended that process bus testing shall concentrate on the issues related to Layer 2 Sampled Values.

- Redundant source failover of subscribing devices.

- System behavior as all SV publishers are failed one at a time (disruptive)

## Substation Maintenance (disruptive)

A set of testcases will be provided so that IED isolation, behavior, simulation, and test modes can ge tested.

# Normal Testing

## SCL

### Test case name:NORM-SCL-01

Configure Client network addressing from SCL

Expected result

4.	Network addressing in Client can be configured from SCL.

5.	Client establishes TPAA with Server.

Test description

Run SCL file through various SCL checkers and validators; report results for documentation.

Start Client without any configuration of a server.

Client selects the server (IED) with which the test is being conducted from the SCD file using local means.

Client shall configure the network addressing information that is necessary for it to establish communication with the selected Server.

While Server is online, establish TPAA from Client.

Comment

tbd: SCL checkers and validators

Link Layer: IP address, IP port

Application Layer ISO 8650-1(ACSE): Calling (client), Called (server)

### Test case name:NORM-SCL-02

Equivalency of Object Model derived from SCL vs. ACSI based discovery

Expected result

5.	The namespace - configured from SCL and available via ACSI. (online) services - are equivalent.

Test description

- Start Client without configuration of Server data model.

- Client selects the server (IED) with which the test is being conducted from the SCD file using local means.

- Client shall configure the server namespace for the IED selected from the SCD file.

- Associate Client and Server.

- Check equivalency of Server data model derived from SCL vs. derived via online services.

Comment

The separate import of the same SCL file for this test may not be required when the namespace has already been configured at test Error! Reference source not found..

It may not be feasible under all circumstances with large data models to perform an exact comparison of the complete data model. Witness to note if the complete data model is compared or a subset of the data model: Logical Device(s), Logical Nodes, Data Objects and/or Functional Constrains.

### Test case name: NORM-SCL-03

Configure RCB Subscription(s) from SCD discovery

Expected result

5.	The Client connects to the Server, enables the RCB and processes Reports.
The Server is providing Reports according to the RCB settings; it provides correct values in URCB.Resv -a) 1, b) 0, BRCB.ResvTms (a) 0, b) -1, and RCB.Owner attributes (if present).

7. 	Client makes correct attempt to enable RCBs - according Client's configuration. 
Server provides correctly updated RCB attributes - according Server's configuration. 
If possible to force mismatch: Server refuses the Client's attempt to enable RCB assigned to mismatching ClientLN.

Test description

- Start Client without configuration of Server's RCBs.

- Using local means Client selects RCBs:

- of own ClientLN (if exist)

- and/or selects instances of not assigned RCBs.

- Using local means Server updates RCBs and/or datasets from SCD/CID.

- Associate Client and Server.

- Client enables RCBs.

- Abort TPAA and reconfigure the Server and/or Client to mismatch ClientLN by a URCB and a BRCB.

- Associate Client and Server. Client attempts to enable RCBs.

Comment

The separate import of the same SCL file for this test case may not be required when the client has already configured the reports in test Error! Reference source not found. or test Error! Reference source not found..

SCT creates SCD based on the ICD/IID files provided by Client and Server:

- New Datasets can be added, or existing can be changed.

- New RCB can be added, or existing attributes can be changed.

- Available ClientLN can be assigned to RCBs in Server's devices.

- Input section with ExtRef can be added to the LN of the Client.

Server shall set non 0 value URCB.Resv and BRCB.ResvTms if RCB is pre-assigned to ClientLN; else 0; then client sets value > 0.

Steps 6-7 are optional as this requires manual manipulation in SCL and/or "freeze" of ConfRev

## Client/Server

### SOE testing (logging mechanism)

Purpose: To verify logging mechanism in close to real life application of SOE between server and clients.

Use cases:

- IED has configured LCB and Log with the same DS that is referenced in URCB. Initiate changes od DO in DS. Compare records in reported URCB and recorded Log (Timestamp, ReasonCode, Value, quality)

- Instantiate 2 LCB (different DS) with same Log. Enable logging and disconnect. Initiate change and connect again with clients to check that all changes are recorded (if PIXIP Lg3 is supported - Multiple Journal Entries).

- Instantiate 2 LCB (same DS) with different Logs. Enable logging. Initiate change DO in DS and connect again with client to check that all changes are recorded in both Logs.

#### Test case name: NORM-LOG-01

IED has configured LCB and Log with the same DS that is referenced in URCB. Initiate changes od DO in DS. Compare records in reported URCB and recorded Log (Timestamp, ReasonCode, Value, quality)

Prerequisites:

IED has been preconfigured (using configuration tool): 
1 x DS with at least 4 DO that can be changed either by simulation or forced externally
1 x URCB with: DatSet = DS, TrgOps= DataChange, OptFlds = all
1 x LCB with: DatSet = DS, LogRef = Log, TrgOps = DataChange

Test steps:

- Connect Client to the IED (server)

- Reserve URCB (set Resv = True)

- Read URCB (request GetURCBValues)

- Enable URCB (set RptEna = True)

- Read LCB (request GetLCBValues)

- Enable LCB (set LogEna = True)

- Initiate several DataChanges of DO within DS in IED and monitor changes in received URCBs.

- Read LCB, verify OldEntrTm, NewEntrTm, OldEnt, NewEnt (request GetLCBValues)

- Read Log entries (QueryLogAfter with no parameters)

- Compare Log and URCB records (Timestamp, Quality, Value, ReasonCode)

- Disable URCB, remove reservation (RptEna = False, Resv = False)

- Disable LCB (set LogEna = False).

Expected results:

- URCB is configured as defined in prerequisites

- URCB is enabled

- LCB is configured as defined in prerequisites

- LCB is enabled

- Verify reports with DataChanges

- OldEntrTm, NewEntrTm, OldEnt, NewEnt changed comparing to initial state from step 3

- Log enties have all records of DataChange with ReasonCode = DataChange

- Reports data correspond to Log data (Timestamp, ReasonCode, Value, quality)

- URCB disabled and reservation removed

- LCB disabled.

#### Test case name: NORM-LOG-02

Instantiate 2 LCB (different DS) with same Log. Enable logging and disconnect. Initiate change and connect again with clients to check that all changes are recorded (if PIXIP Lg3 is supported - Multiple Journal Entries).

Prerequisites:

IED has been preconfigured (using configuration tool): 
2 x DS’s with at least 4 DO that can be changed either by simulation or forced externally
1 x LCB1 with: DatSet = DS1, LogRef = Log, TrgOps = DataChange
1 x LCB2 with: DatSet = DS2, LogRef = Log, TrgOps = DataChange

Test steps:

- Connect Client to the IED (server)

- Read LCB1 (request GetURCBValues)

- Enable LCB1 (set LogEna = True),

- Read LCB2 (request GetURCBValues)

- Enable LCB2 (set LogEna = True)

- Disconnect Client from IED.

- Initiate several DataChanges of DO within DS1 and DS2 in IED.

- Connect Client to the IED (server)

- Read LCB1 and LCB2, verify OldEntrTm, NewEntrTm, OldEnt, NewEnt (request GetLCBValues)

- Read Log entries (QueryLogAfter with no parameters)

- Disable LCB1, LCB2 (set LogEna = False).

Expected results:

- LCB1 is configured as defined in prerequisites

- LCB1 is enabled

- LCB2 is configured as defined in prerequisites

- LCB2 is enabled

- OldEntrTm, NewEntrTm, OldEnt, NewEnt changed comparing to initial (read in LCB1 and LCB2 step 2 and 4). Values in LCB1 and LCB2 are same (at least OldEntrTm, NewEntrTm)

- Log enties have all records of DataChange with ReasonCode = DataChange. Timestamp, ReasonCode, Value and quality correspond to initiated values.

- LCB1 and LCB2 disabled.

#### Test case name: NORM-LOG-03

Instantiate 2 LCB (same DS) with different Logs. Enable logging. Initiate change DO in DS and connect again with client to check that all changes are recorded in both Logs.

Prerequisites:

IED has been preconfigured (using configuration tool): 
1 x DS’s with at least 4 DO that can be changed either by simulation or forced externally
1 x LCB1 with: DatSet = DS1, LogRef = Log1, TrgOps = DataChange
1 x LCB2 with: DatSet = DS1, LogRef = Log2, TrgOps = DataChange

Test steps:

- Connect Client to the IED (server)

- Read LCB1 (request GetURCBValues)

- Enable LCB1 (set LogEna = True),

- Read LCB2 (request GetURCBValues)

- Enable LCB2 (set LogEna = True)

- Initiate several DataChanges of DO within DS1 in IED.

- Read LCB1 and LCB2, verify OldEntrTm, NewEntrTm, OldEnt, NewEnt (request GetLCBValues)

- Read Log entries (QueryLogAfter with no parameters)

- Disable LCB1, LCB2 (set LogEna = False).

Expected results:

- LCB1 is configured as defined in prerequisites

- LCB1 is enabled

- LCB2 is configured as defined in prerequisites

- LCB2 is enabled

- OldEntrTm, NewEntrTm, OldEnt, NewEnt changed comparing to initial (read in LCB1 and LCB2 step 2 and 4). Values in LCB1 and LCB2 are same (at least OldEntrTm, NewEntrTm)

- Log entries have all records of DataChange with ReasonCode = DataChange. Timestamp, ReasonCode, Value and quality correspond to initiated values

- LCB1 and LCB2 disabled.

### Data acquisition of FCD or FCDA

This section shall verify acquiring data (service: Read a/o Report) at the various levels of Object Reference.

#### Test case name: NORM-FCD-01

#### Test case name: NORM-FCD-02

Expected result

1.	Client values of the Server’s data attributes of FC in acquired DO match. 
For Data Objects with FC=ST/MX also Quality and Timestamp match.

Test description

- Client issues a Read (or process Report) of a FCD, e.g. LLN0.Mod and FC=ST.

Comment

#### Test case name: NORM-FCDA-01

Expected result

1, 3.	Client value of the Server’s data attribute matches. 
On Client the Quality of Data Object - if not acquired separately - stays unchanged or changes to local default value.
On Client the Timestamp of Data Object is local.

Test description

- Client issues a Read (or process Report) of a FCDA, e.g. LLN0.Mod.stVal

- In case of ST/MX data attributes: force on Server the change of Quality and Timestamp of the Data Object.

- Client issues a Read (or process Report) of the FCDA.

Comment

Observer takes note what (local meanings) Server and Client are using to assure that Data Object (of CDC listed in -7-2 Table 64, q and t) with ST/MX has Quality and Timestamp in case of access limited to FCDA level

#### Test case name: NORM-READ-FLOAT

Expected result

1..4. Client value of the Server’s Floating-point value shall match within possible rounding errors.
Also Quality and Timestamp shall match if q and t are included.

Test description

- Client and Server are to process a Read service at the DO, DA and/or other node levels:

- Level of DO, e.g. MMXU1.PhV.phsA [MX]

- Level of DA, e.g. MMXU1.PhV.phsA.cVal.mag.f [MX]

- Level of part of structured DO, e.g. MMXU1.PhV [MX]

- Level of part of structured DA, e.g. MMXU1.PhV.phsA.cVal [MX]

Comment

Float attribute to be selected from Server’s data model.

Observer takes note what (local meanings) Server and Client are using to assure that MX data has Quality and Timestamp in case of access limited to FCDA level.

#### Test case name: NORM-FLOAT-02

Expected result

1..4. Client value of the Server’s Floating-point value shall match within possible rounding errors.
Also Quality and Timestamp shall match if q and t are included in referred part.

Test description

- Client is to acquire Reports with float at the DO, DA and/or other node levels:

- Level of DO, e.g. MMXU1.PhV.phsA [MX]

- Level of DA, e.g. MMXU1.PhV.phsA.cVal.mag.f [MX]

- Level of part of structured DO, e.g. MMXU1.PhV [MX]

- Level of part of structured DA, e.g. MMXU1.PhV.phsA.cVal [MX]

Comment

Float attribute to be selected from Server’s data model.

Observer takes note what (local meanings) Server and Client are using to assure that MX data has Quality and Timestamp in case of access limited to FCDA level.

### Datasets

This section shall verify Datasets containing members at various Object Reference levels.

#### Test case name: NORM-DATASET-01

Reason: FCD and FCDA in predefined Dataset

Expected result

1.	Client values of the members of the dataset match with the Server.

Test description

- Perform GetDataSetValues and data-change Report on a predefined dataset with at least 4 members:

  - with at least one member being a FCD;

  - with at least one member being a FCDA.

Comment

Observer takes note if Dataset members are FCD or FCDA and takes note of what (local meanings) Server and Client are using to assure that MX data has Quality and Timestamp in case of access limited to FCDA level.

#### Test case name: NORM-DATASET-02

Reason:Array in predefined Dataset

Expected result

1.	Client values of the members of the dataset match with the Server.

Test description

- Perform GetDataSetValues and data-change Report on a dataset that contains members of datatype ARRAY.

Comment

Observer notices if Dataset members are FCD or FCDA with indexing. 
Example of FCDA with indexing (from part 6):
<FCDA ldInst="C1" lnInst="1" lnClass="PVOC" doName=" TmASt " fc="SP" daName="curvPts(2).xVal" ix="2"/>

<FCDA ldInst="C1" lnInst="1" lnClass="MHAI" doName="HPhV.phsAHar(3)" fc="MX" daName="mag" ix="3"/>

#### Test case name: NORM-DATASET-03

Reason: FCD and FCDA in dynamic Dataset

Expected result

1.	DataSet on Server is defined correctly.

2.	Client values for the members of the data set should match those of Server.

3.	DataSet is deleted from Server.

Test description

- CreateDataSet with at least 4 members:

  - with at least one member being a FCD;

  - with at least one member being a FCDA.

- Perform GetDataSetValues (or Report) on the dataset.

- DeleteDataSet (created in step 1).

Comment

Observer takes note of what (local meanings) Server and Client are using to assure that ST/MX data has Quality and Timestamp in case of access limited to FCDA level.

### Reporting

The previous test cases are already covering basic scenarios for RCB enable and data acquisition via Reporting. This section shall verify more sophisticated or (system) specific dependencies resulting from flexibility of the Standard.

The focus is also how to detect and solve situations resulting from configuration (SCL, human) mistakes via online services.

#### Test case name: NORM-RPT-01

Reason: Initial RCB enable

Expected result

1.	Client is able to enable RCB.

2.	Client is able to update RCB and enable it. 
Server accepts SetRCBValues of "Dyn" attributes.

3.	Server and Client process Report services. 
Server process Report according RCB attributes. 
Client gives some indication that data being acquired via reporting. 
Client values (and quality and timestamp) match those of Server.

Test description

- Enable RCB with "Fix/Conf" attributes fulfilling minimal Client's requirements.

- SetRCBValues on "Dyn" attributes: TrgOps, OptFlds, IntgPd, BufTm; then enable RCB.

- Process Reports on triggers: GI or integrity, and on data-change.

Comment

Minimal RCB attributes requirements are in client's PIXIT (not ICD), thus in SCD a mismatch is possible.

#### Test case name: NORM-RPT-02

Reason: Release RCB.RptEna by connection loss

Expected result

3.	Client and Server detect connection loss.
Client gives indication of connection loss.
Server sets RptEna = false in all RCBs assigned to the Client.

4. 	Client and Server associate and enables the RCBs successfully.

Test description

- Associate Client and Server.

- Client enables at least one URCB and one BRCB.

- Disconnect Ethernet between Client and Server.

- Reconnect Ethernet, associate Client and Server and enables the RCBs.

Comment

Prefer to use the loss detection via mandatory TCP_KEEPALIVE, not local loss of TCP link; and not via MMS services (no/slow Integrity, no/slow polling).

Note: URCB.Resv and BRCB.ResvTms handling will be tested in a next case.

#### Test case name: NORM-RPT-03

Reason: RCB without Dataset

Expected result

1.	optionally, in case the Server does not support dynamical datasets:
Server allows only RCB to be configured with a valid Datset. Server's ICT gives indication about the case.

3.	Depending step 1 and local meanings in Server and Client:

- Client detects missing/invalid Dataset in the RCB and gives indication about the case. Client does not try to enable RCB or configures dynamical or an existing dataset.

- While RCB.Datset is invalid, Server responds SetRCBValues( RptEna) negative.

Test description

- Configure Server to have a RCB with empty (or not existing) Datset attribute.

- Configure Client to try to enable the RCB.

- Associate Client and Server. Force Client to SetRCBValues( RptEna ).

Comment

#### Test case name: NORM-RPT-04

Reason: Empty or ambiguous Report ID

Expected result

2.	Client enables RCB.

3.	Server provides the correct RCB reference in Report.RptID value.
Client values of the members of the dataset should match those of Server.

5.	Client may (try to) update RptID or OptFlds.
Server accepts updates (if related ReportSettings are "Dyn").
Client enables updated RCB or indicates failure.

6. 	If update was possible the Client values of the members of the dataset should match those of Server.

Test description

- Configure Server to have a RCB with empty RptID attribute and minimal required OptFlds by the Client.

- Associate Client and Server. Client to enable the RCB.

- Process (in Server and Client) at least one Report on data- or quality-change and one GI or Integrity.

- Abort TPAA and configure Server to have 2 RCBs with identical RptID but different Dataset. Configure RCBs with OptFlds not containing data-set-name nor data-reference.

- Associate Client and Server. Client enables the RCBs or indicates failure.

- For both RCBs: process (in Server and Client) at least one Report on data- or quality-change and one GI or Integrity.

Comment

#### Test case name: NORM-RPT-05

Reason: Analogue (MX) data Reports dependency to BufTm and Deadband

Expected result

3, 6.	Server process Reports according BufTm and correctly applies the deadband for the measured values - from instant values, considering deadband (the attribute db [CF]).
Client values of the Server’s measured values shall match within possible rounding errors.

Test description

- Configure Server to have a RCB with deadbanded, analogue values, 
e.g. attribute mag in the CDC MV like MMXU1.PhV.phsA [MX].

- Associate Client and Server. Client enables the RCB.

- Process at least one Report on data-change or data-update.

- Abort TPAA or disable RCB; reconfigure RCB.BufTm and MMXU1.PhV.phsA.db [CF] in SCL or via online services.

- (Associate) Client enables the RCB.

- Process at least one Report on data-change or data-update.

Comment

RCB.BufTm and db [CF] are parameters making possible to limit Ethernet traffic caused by reporting of measured values; the use-case are instantly fluctuating measured values. The data attribute db is optional in CDC MV. If the db attribute is a member of Dataset is not relevant for the test.

#### Test case name: NORM-RPT-06

Reasone: URCB.Resv handling by connection loss

Expected result

1.	Server sets URCB.Resv = true in preassigned URCB.

2. 	Client does not SetURCBValues( Resv ) or accepts (p/n) response; and enables the URCB correctly.

3. 	Server and Client detects connection loss. The value of URCB.Resv does not change.

4.	Server sets URCB.Resv = false.

5.	Client does SetURCBValues( Resv=true ) and enables the URCB.

6. 	Server and Client detects connection loss. Server changes URCB.Resv to false.

Test description

- Configure in Server an URCB with an instance preassigned to ClientLN of the Client.

- Associate Client and Server. Client enables the URCB.

- Abort TPAA.

- Configure in Server an URCB without any ClientLN.

- Associate Client and Server. Client enables the URCB.

- Abort TPAA.

Comment

Results depend on Ed.1 / Ed.2. Observers may notice the meanings the Client and the Server are using to solve eventual differences in reservation handling.

#### Test case name: NORM-RPT-07

Reason: Acquisition of Reports buffered during TPAA loss

Expected result

4.	Client sends correct EntryID - the last completely received before TPAA loss.
Server:

- if no buffer overflow:  responds EntryID positive;

- buffer overflow:  responds EntryID negative and in step 5 process like EntryID=0 - sends from the first entry in the buffer.

5. 	Server sends Reports starting by next after received EntryID or all buffered in case of overflow. In case of overflow, if OptFlds, the BufOvfl is in the first Report.
Client process data from buffered reports and gives some indication that data being acquired via reporting and in case of overflow. Client values (and quality and timestamp) match those of Server also for data from period of connection loss.

7. 	Results depend if Client uses resynchronization (a) 
or mismatch detection/auto-description (b):

- Server responds EntryID negative and in step 8 process like EntryID=0 - sends from the first entry in the buffer.

- Client resynchronizes using EntryID=0 or SetBRCBValues( PurgeBuf and/or GI)

8. 	 Client process data from buffered reports and gives some indication that data being acquired via reporting.
If buffer is purged, and if OptFlds, Server sets BufOvfl in the first Report.

Test description

- Associate Client and Server, Client enables at least one BRCB.

- Server and Client process at least one Report with valid EntryID. Then force TPAA loss.

- During connection loss Server buffers at least one data- or quality-change report.

- Associate Client and Server. Client resynchronizes the BRCB - SetBRCBValues( EntryID).

- Client enables the BRCB and process buffered Reports.

- Force TPAA loss and reconfigure on Server some members of Dataset in the BRCB.

- Associate Client and Server. Client resynchronizes the BRCB or - if detects mismatch or uses auto-description - it purges the buffer.

- Client enables the BRCB and process buffered Reports or GI.

Comment

According IEC 61850-7-2, 17.2.2.1, a server shall first respond SetBRCBValues( EntryID ) and then may send Reports. And - according TISSUE 1454 - a server may send Report by reception of SetBRCBValues( RptEna ) - already before the write response. Thus the test result depends if Client maps SetBRCBValues for EntryID and RptEna in only one, or few MMS services.

#### Test case name: NORM-RPT-08

Reason:  BRCB.ResvTms handling by connection loss

Expected result

1.	Server sets BRCB.ResvTms = -1 in pre-assigned URCB.

2. 	Client does not SetBRCBValues( ResvTms ) or accepts (p/n) response; and enables the BRCB correctly.

3. 	Server and Client detects connection loss. The value of BRCB.ResvTms = -1 not change.

4.	Server sets BRCB.ResvTms = 0.

5.	Client does SetBRCBValues( ResvTms > 0 ) and enables the BRCB.

6. 	Server and Client detects connection loss. Server counts down BRCB.ResvTms.

Test description

- Configure in Server a BRCB with an instance preassigned to ClientLN of the Client.

- Associate Client and Server. Client enables the BRCB.

- Abort TPAA. Use local Server's meanings of additional client to check BRCB attributes.

- Configure in Server a BRCB without any ClientLN.

- Associate Client and Server. Client enables the BRCB.

- Abort TPAA. Use local Server's meanings of additional client to check BRCB attributes.

Comment

BRCB.ResvTms is optional. Results depend on Ed.1 / Ed.2. Observers may notice the meanings the Client and the Server are using to solve eventual differences in reservation handling.

#### Test case name: NORM-RPT-09

Reason: Data in Reports from BRCB instances enabled by redundant Clients

Expected result

5.	During connection loss Server process Reports for connected Client with identical data (value, quality and timestamp) as data in buffered Reports processed to second Client.
On both Clients, the values of the members of the dataset should match those of Server.

Test description

- Configure system where 2 BRCBs with the same Dataset are enabled by duplicated (redundant) Clients, e.g. use two instances of a BRCB.

- Associate Server with both Clients. Enable reporting, produce at least one Report.

- Disconnect Ethernet by one Client.

- Process few Reports on trigger data-change.

- (re)Associate the Client. Client acquires buffered data.

Comment

Demands redundant clients or the compare using two clients configured in parallel.

### Control Services

Cases are focusing on tracking of control services in multi-clients systems.

#### Test case name: NORM-CNTRL-01

Reason: Tracking of service Select/SelectWithValue negative

Expected result

3.	Server process Service Tracking about the control service with correct information (ServiceType, ErrorCode, originator, AddCause etc).
Client gives indication about the control service processed by another client.

Test description

- Configure reporting of LTRK.SpcTrk or LTRK.DpcTrk.

- Associate Client and Server.

- Another client process Select or SelectWithValue on interlocked or already selected SPC or DPC in control mode 2 or 4.

Comment

Ed.2 only.
Demands use of multiple clients.

#### Test case name: NORM-CNTRL-02

Reason: Tracking of service Operate from another client

Expected result

3.	Similar like 0; 
Optional test of the use-case: suppressing of trip detection on Client.

Test description

- Configure reporting of LTRK.SpcTrk or LTRK.DpcTrk.

- Associate Client and Server.

- Another client process successfully Operate on SPC or DPC.

Comment

Ed.2 only.
Demands use of multiple clients.

### Settings Group

#### Test case name: NORM-SGCB-01

Reason: Ability to change Active Group

Expected result

1.	Active setting group is changed

2. Settings are shown to have actually been changed.

Test description

1.  Client changes active setting group

#### Test case name: NORM-SGCB-02

Reason: Ability to change setting and then activate the revised group

Expected result

1.	Active setting group is changed

2. Settings are shown to have actually been changed.

Test description

- Client sets edit group.

- Client changes a setting as is appropriate (must coordinate with IED vendor).

- Client saves group.

- Client activates group.

#### Test case name:NORM-SGCB-03

Reason: Verification that Setting Group Change are persisted

Expected result

1.	Active setting group is changed

2. Settings are shown to have actually been changed.

Test description

- Client changes active setting group

- DUT is power-cycled

- Client re-establishes connection.

- Client verifies active setting group.

#### Test case name: NORM-SGCB-04

Reason: Verification that Setting Changes are persisted

Expected result

1.	Active setting group is changed

2. Settings are shown to have actually been changed.

Test description

- Client sets edit group.

- Client changes a setting as is appropriate (must coordinate with IED vendor).

- Client saves group.

- DUT is power-cycled

- Client re-establishes association.

- Client activates group.

#### Test case name:NORM-SGCB-NEG-01

Reason: Verification that Settings are persisted

Expected result

1.	Active setting group is changed

2. The settings are shown to have not  changed.

Test description

- Client sets edit group.

- Client changes a setting as is appropriate (must coordinate with IED vendor).

- Client cancels the edit.

- Client activates group.

## GOOSE

Precondition:  LLN0.Mod should be set to a value of ON.  All participating LNx.Mod value should be ON.  The LLN0.Beh value should reflect a value of ON (same with the LNx values).   This needs to be verified through HMI/Client interaction and represents a test case as part of the client/server part of this test.

### IEDs can ignore simulated data

#### Test case name: NORM-GOOSE-01

Reason: To make sure that IEDs process the appropriate information as part of a normal maintenance process.

Test steps:

- LPHD.Sim is set to false in the IED under test.

- Test set is configured to emulate all the GOOSE messages for which an IED subscribes for from a particular IED.

- Test set begins publishing the GOOSE messages with the Simulation bits set and data quality=good.

Expected Results:

- Because LPHD.Sim is false, It is expected that the IED under test will not take action on the test set information.

- If there is a monitoring substation HMI/Client (s), the instance of LGOS should be checked and normal operation of LGOS.NdsCom=false, LGOS.LastStNum should have good quality, LGOS.St shoud be True with good quality, LGOS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LGOS.SimSt should be false.

- The rest of the IEDs in the system should be unaffected. How do we observe this?

#### Test case name: NORM-GOOSE-02

Reason: To make sure that IEDs process the appropriate information as part of a normal maintenance process.

Test steps:

- LPHD.Sim is set to false in the IED under test.

- Test set is configured to emulate all the GOOSE messages for which an IED subscribes for from a particular IED.

- Test set begins publishing the GOOSE messages with the Simulation bits set and data quality=good.

- The LPHD.Sim value is set to true in the IED under test.

- After some time, and observing the reaction of the IED under test, set the LPHD.Sim value to false in the IED under test.

Expected Results:

- After step 3, it is expected that the IED under test will not take action on the test set information.

  - If there is a monitoring substation HMI/Client (s), the instance of LGOS should be checked and normal operation of LGOS.NdsCom=false, LGOS.LastStNum should have good quality, LGOS.St shoud be True with good quality, LGOS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LGOS.SimSt should be false.
The witness should note that value of LGOS.LastStNum as it will be used for the next step expected results.

- After step 4, it is expected that the IED under test will take action on the test set information.

  - If there is a monitoring substation HMI/Client (s), the instance of LGOS should be checked and normal operation of LGOS.NdsCom=false, LGOS.LastStNum should have good quality, LGOS.St shoud be True with good quality, LGOS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LGOS.SimSt should be true.  
It is highly probable that the LGOS.LastStNum value will be different than the one observed in step 1.  This would be typical and is worthwhile to check.  
The value should be recorded prior to the next test step execution.

  - The other IEDs in the system should be unaffected.  How do we observe this?

- After step 5, it is expected that the IED under test will not take action on the test set information.

If there is a monitoring substation HMI/Client (s), the instance of LGOS should be checked and normal operation of LGOS.NdsCom=false, LGOS.LastStNum should have good quality, LGOS.St shoud be True with good quality, LGOS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LGOS.SimSt should be false.
It is highly probable that the LGOS.LastStNum value will be different than the one observed in step 1.  This would be typical and is worthwhile to check.

#### Test case name: NORM-GOOSE-03

Reason: To make sure that all IEDs which are currently not being tested ignore the simulated GOOSE.

Test steps:

- LPHD.Sim is set to false in the IED under test.

- Test set is configured to emulate all the GOOSE messages for which an IED subscribes for from a particular IED.

- Test set begins publishing the GOOSE messages with the Simulation bits set and data quality=good.

Expected Results:

- After step 3 it is expected that the IED under test will not take action on the test set information.

- If there is a monitoring substation HMI/Client (s), the instance of LGOS should be checked and normal operation of LGOS.NdsCom=false, LGOS.LastStNum should have good quality, LGOS.St shoud be True with good quality, LGOS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LGOS.SimSt should be false.

- The rest of the IEDs in the system should be not operate upon the information provided by the IED under test.

## Sampled Values

### Tests of behavior of LPHD.Sim

#### Test case name: NORM-SV-01

Reason: To make sure that IEDs process the appropriate information as part of a normal maintenance process.

Test steps:

- LPHD.Sim is set to false in the IED under test.

- Test set is configured to emulate all the SV messages for which an IED subscribes for from a particular IED.

- Test set begins publishing the SV messages with the Simulation bits set and data quality=good. The test set contains a fault current in the SV messages in attempt to trip the IED.

Expected Results:

- It is expected that the IED under test will not take action on the test set information.

- If there is a monitoring substation HMI/Client (s), the instance of LSVS should be checked and normal operation of LSVS.NdsCom=false,  LSVS.St shoud be True with good quality, LSVS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LSVS.SimSt should be false.

- The rest of the IEDs in the system should be unaffected. How do we observe this? A measurement value in the IED not affected could be observed.

#### Test case name: NORM-SV-02

Reason: To make sure that IEDs process the appropriate information as part of a normal maintenance process.

Test steps:

- LPHD.Sim is set to false in the IED under test.

- Test set is configured to emulate all the SV messages for which an IED subscribes for from a particular IED.

- Test set begins publishing the SV messages with the Simulation bits set and data quality=good. The test set contains a fault current in the SV messages to trip the IED.

- The LPHD.Sim value is set to true in the IED under test.

- After some time, and observing the reaction of the IED under test, set The LPHD.Sim value is set to false in the IED under test.

Expected Results:

- After step 3, it is expected that the IED under test will not take action on the test set information.

  - The IED shall use the not-simulated values.

  - If there is a monitoring substation HMI/Client (s), the instance of LSVS should be checked and normal operation of LSVS.NdsCom=false, LSVS.St shoud be True with good quality, LSVS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LSVS.SimSt should be false.

- After step 4, it is expected that the IED under test will take action on the test set information.

  - The IED shall use the simulated values.

  - If there is a monitoring substation HMI/Client (s), the instance of LSVS should be checked and normal operation of LSVS.NdsCom=false, LSVS.St shoud be True with good quality, LSVS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LSVS.SimSt should be true.

  - The other IEDs in the system should be unaffected.  How do we observe this?  Check the response of their protection function (which should be ignoring the simulated SV).

- After step 5, it is expected that the IED under test will not take action on the test set information.

  - If there is a monitoring substation HMI/Client (s), the instance of LSVS should be checked and normal operation of LSVS.NdsCom=false,  LSVS.St shoud be True with good quality, LSVS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LSVS.SimSt should be false.

### Redundant Merging Unit

In a digital substation, Stand Alone Merging Unit (SAMU) provides information from primary equipment to the protective relays via an ethernet network. This information is used for the protection and control of these equipment. To minimize single point of failure and improve the availability of a protection system, redundant SAMUs, redundant protection communications network, and redundant protective relays are often applied. Many breaker and transformer cabinets have redundant current transformers installed in them. It makes sense to install redundant SAMUs in these cabinets to avoid single point of failure. When a redundant SAMU is not available locally, other SAMUs in the system can also act as a redundant unit. A protective relay subscribes to data from primary SAMUs and the redundant SAMUs. When primary SAMUs are available, the protective relay uses its data from protection and control. If a primary SAMU fails, the protective relay can switch to the redundant SAMU to keep the protection system available.

Figure 6 shows a section of the single line diagram from Figure 2 (General Integrated Application Test Cases – IOP 2019). The transformer relay (TXA_IED) protects the transformer using two primary SAMUs, TXA_MU01 and TXA_MU02. The sum of currents measured by feeder SAMUs, A1_MU and A2_MU, is same as that of current measured by TXA_MU02. Hence, two feeder SAMUs, A1_MU and A2_MU, can act as redundant SAMU for TXA_MU02. When TXA_MU02 is healthy, TXA_IED provides differential protection to Transformer A using TXA_MU01 and TXA_MU02 SAMUs. If TXA_MU02 fails, it will be replaced by A1_MU and A2_MU in TXA_IED for differential protection.

Figure 6: Primary and redundant SAMUs for a transformer IED

Initial Configuration:

Following steps are required to create an operational system before executing two test cases below.

- Configure TXA_IED to subscribe SV streams from four SAMUS, i.e., TXA_MU01, TXA_MU02, A1_MU, and A2_MU

- Map three phase currents from the TXA_MU01 to Current Terminal #1 in the TXA_IED.

- Map three phase currents from the TXA_MU02 to Current Terminal #2 in the TXA_IED.

- Sum three phase currents from A1_MU and A2_MU and map it to Current Terminal #3 in the TXA_IED.

- Configure transformer differential protection (87T) to use Current Terminals as shown below:

  - Terminal #1 and Terminal #2 when TXA_MU02 is healthy

  - Terminal #1 and Terminal #3 when TXA_MU02 is unavailable

- Configure transformer differential protection (87T) for Transformer A parameters shown in the figure.

#### Test case name: NORM-SV-RED-SAMU-01

Precondition: All SAMUs are operating under normal conditions.

Test steps:

- Apply current signals to all four SAMUs. Apply currents in such a way that power flows from the transformer to two feeders (Normal condition).

- Use IED metering function to read the current of all three current terminals.

- Use IED built-in function to verify Current Terminals used for transformer differential protection (87T).

- Apply currents associated with transformer internal fault to all four SAMUs (Fault condition).

- Apply current signals from test step 1.

Expected results:

- After step 1, it is expected that the IED subscribes to SV streams from all four SAMUs.

- After step 2, the IED metering functions shall correctly display the current signals measured by all four SAMUs.

- After step 3, the IED shall indicate that it uses Current Terminal #1 (TXA_MU01) and Current Terminal #2 (TXA_MU02) for transformer differential protection (87T).

- After step 4, the IED’s transformer differential protection (87T) shall operate to indicate internal fault.

- After step 5, the IED metering functions shall correctly display the current signals measured by all four SAMUs.

#### Test case name: NORM-SV-RED-SAMU-02

SAMU: sending SV on multiple SV flux

Purpose:

Verify that a SAMU can send its sample values on several flux, so that each protection get only their data.

A typical use casa is as follow:

- The “line” is a combination of cable and overhead lines.

PreCondition

The following devices shall be on and configured as follow:

- One SAMU is sampling 3CT, the 3 VT and an I0 CT.

- A distance protection (IED1), need 3I and 3 voltages

- A frequency protection (IED2, need 3 voltages

- A cable protection (IED3), need only I0.

- The three SV flux for IED1A, IED2, and IED3 have a specific SV_ID and SV Control block and can trip the breaker independently.

Why ?

- This is to mimic the traditional implementation with the wires: each protection is connected to the appropriate voltage and current.

Verification

- The  three  relays are receiving and using the individual flux.

- Appropriate fault injection allows to verify each protection individually thanks to the separated SV_ID / VLAN / SC Control block

Investigation / disruptive case:

- The SV flux from A is interrupted during a short period of time (100ms)

- After this delay, a fault is injected on B

- goal determine how long it takes to change-over

#### Test case name: NORM-SV-RED-SAMU-03

Purpose:

Verify that a protection relay can switch from a SV flux to another

PreCondition

The following devices shall be on and configured as follow:

- One Samu device (‘SAMUA’) is set-up so that a protection relay can use a simple SV flux from it.

- A second Samu (‘SAMUA’) device, set-up so that the same protection relay can also subscribe simple SV flux from it.

- SAMUA and SAMUB have different destination MAC address for their SV flux as well as different smvID

- The SV flux from A consist in nominal Voltage and typical current (no fault injected).

- The SV flux from B consist in half the Voltage and half the current compared A (or another way to be sure which one is being used, but not 0…)

- The protection is initially using the flux from SAMUA ( ? not obvious)

- The protection can display average value from the SV received

PreCondition verification

- The protection relay show the value of the flux A on the local HMI.

- SvScout / WireShark is used to check the validity of both SV flux.

Trigger case / expected behavior:

- SAMU A is turned off

  - The protection relay show the value of the flux B on the local HMI.

  - There is no changes in *.Heath Data Object (several DO might be available).

  - There is “another event” that should be visible regarding the loss of SAMU A, on the IHM.

- Both SAMU are on

Step1

  - On SAMU A, the injection of I/U is modified so that the quality of one or several TVTR.VolSv is invalid

  - Change Over is expected

Step 2

  - Back to initial status

  - The quality of one or several TCTR.AmpSv is invalid or questionable.

Investigation / disruptive case:

- The SV flux from A is interrupted during a short period of time (100ms)

- After this delay, a fault is injected on B

- goal determine how long it takes to change-over

On a given bay we have:

  - One SAMU has its LPHD.Health set to Warning or Alarm.

  - The quality of one or several TVTR.VolSv is invalid or questionable.

  - The quality of one or several TCTR.AmpSv is invalid or questionable.

- We are looking at one given failure at a time. We do not expect the relay to use Voltages from A and Currents from B for example.

#### Test case name: ABN-SV- RED-SAMU-01

Preconditions: All SAMUs are operating under normal conditions.

Test steps:

- Apply current signals to all four SAMUs. Apply currents in such a way that power flows from the transformer to two feeders (Normal condition).

- Use IED metering function to read the current of all three current terminals.

- Use IED built-in function to verify Current Terminals used for transformer differential protection (87T).

- Disrupt power to TXA_MU02 SAMU.

- Use IED metering function to read the current of all three current terminals.

- Use IED built-in function to verify Current Terminals used for transformer differential protection (87T).

- Apply currents associated with transformer internal fault to all four SAMUs (Fault condition).

- Apply current signals from test step 1.

Expected results:

- After step 1, it is expected that the IED subscribes to SV streams from all four SAMUs.

- After step 2, the IED metering functions shall correctly display the current signals measured by all four SAMUs.

- After step 3, the IED shall indicate that it uses Current Terminal #1 (TXA_MU01) and Current Terminal #2 (TXA_MU02) for transformer differential protection (87T).

- After step 4, the IED shall lose SV subscription from TXA_MU02 SAMU. SV streams from remaining three SAMUs shall be good.

- After step 5, the IED metering functions shall correctly display the current signals measured by TXA_MU01 and A1_MU+A2_MU SAMUs. The current measurement at Terminal #2 shall be 0.

- After step 6, the IED shall indicate that it uses Current Terminal #1 (TXA_MU01) and Current Terminal #3 (A1_MU+A2_MU) for transformer differential protection (87T).

- After step 7, the IED’s transformer differential protection (87T) shall operate to indicate internal fault.

- After step 8, the IED metering functions shall correctly display the current signals measured by TXA_MU01 and A1_MU+A2_MU SAMUs.

# Substation Maintenance

## Change SCD Communication Configuration: DIS-SCL-01

## IED Addition to Bay or Additional Bay

Purpose:  To verify the engineering process required to add a new IED into an existing IEC 61850 system, including:

- SCT can import SCD file

- SCT can import ICD file of the IED

- SCT can configure communication parameters

- SCT can perform dataflow (DataSets, Reports, GOOSE, SV) and Log engineering within the limits declared as part of the capabilities in the service section

- SCT can draw single line diagram

- SCT can draw communication diagram

- SCT can create a valid SCD file

- ICT can accept modifications in the communication section (e.g. Subnet name, IP address), IED section (e.g. LN attribute lnType), and data type template section (e.g. LNodeType attribute id) as they are required to build a consistent SCD file.

- ICT can accept configurations of Report, GOOSE, SV and Log control blocks and data sets from an SCD file if they are within the limits declared as part of the capabilities in the service section and or PIXITS.

- ICT can import and use GOOSE and SV subscription information from other IEDs contained within the SCD file.

- ICT can accept instantiations of IEDs based on ICD files through an SCD file.

- ICT can configure IED to perform implemented protection and control schemes.

Preconditions and explanation:

Adding an IED into an existing IEC 61850 system requires a “round trip” engineer cycle involving the System Configuration Tool and all IEDs (and their respective IED Configuration Tools) that exchange data with the new IED.  Therefore, these tests require the cooperation of several parties.

Test Support	Delivers

- SCD file

- ICD file for the IED being added

Participant SCT	Prepares

- SCT with SCD and ICD file from test support already processed (SICS S23, S41)

Participant ICT	Prepares

- ICT with ICD file for the IED that will be physically present in the test

### Test case name: SUBMAINT-01

Description: Verify Engineering with SCT

Test Steps:

- Check SCD file

  - Run SCD file through various SCL checkers and validators; report results for documentation

- Check ICD file

  - Run ICD file through various SCL checkers and validators; report results for documentation

- SCT imports SCD file

  - SCT is able to import SCD file	(SICS S71, S72)

- SCT imports ICD file and creates the instance of IED

  - SCT is able to import ICD file and to create instance	(SICS S11 – S15, S111)

- SCT adds the new IED to the already existing subnetwork modifying possibly predefined addressing information as required

  - (SICS S21, S22)

- SCT associates the LNs in the IED to the related LNs in the single line diagram / substation section

  - (SICS S43)

- SCT adds the new IED to the communication diagram and configures physical connections (PhysConn)

  - (SICS S24)

- SCT configures datasets and report control blocks with the data required to be transmitted to the gateway and to the local HMI (if supported by the IED) including configuration of ClientLN and trgOps

  - Verify that tool does not provide capability to configure / change dataset and report control block if not allowed by the IED	(SICS S56)

- SCT configures signal flow, GOOSE control blocks, SV control blocks and associated datasets to implement the needed functions

  - Verify that tool does not provide capability to configure / change dataset and GOOSE/SV control block if not allowed by the IED	(SICS S56)

- SCT configures Log control blocks and associated datasets

  - Verify that tool does not provide capability to configure / change dataset and Log control block if not allowed by the IED	(SICS S56)

- SCT exports SCD file

  - SCT is able to produce SCD file	(SICS S61, S62, S64, S66, S67)

### Test case name: SUBMAINT-02

Description: SCD file inspection

Test Steps:

- Verify step A4

  - In the SCD file, verify that IED section has been added for the IED

- Verify step A5

  - In the SCD file, verify that the IED have been added in the communication section to the already existing subnetwork	(SICS S22)

- Verify step A6

  - In the SCD file, verify the association of the LNs from the IED with the respective LNs in the substation section	(SICS S43)

- Verify step A7

  - In the SCD file, verify that PhysConn elements are configured	(SICS S24)

- Verify step A8

  - In the SCD file, verify that the report control blocks and data sets are configured	(SICS S31 – S35, S56)

- Verify step A8

  - In the SCD file, verify that the ClientLN element is configured for the report control blocks	(SICS S361)

- Verify step A9

  - In the SCD file, verify that GOOSE/SV control blocks and data sets are configured	(SICS S31 - S35, S56)

- Verify step A9

  - In the SCD file, verify that IEDName elements are configured for GOOSE and SV messages	(SICS S361)

- Verify step A9

  - In the SCD file, verify that the data subscription is configured (input section and external references)	(SICS S37, S381, S382, S39)

- Verify step A10

  - In the SCD file, verify that Log control blocks and data sets are configured (SICS S31-35, S56)

- Check SCD file

  - Run SCD file through various SCL checkers and validators; report results for documentation.

### Test case name: SUBMAINT-03

Description: Engineering with ICT

Test Steps:

Note: Steps C1 – C5 should be done for the newly added IED and for all existing IEDs that are receiving data from the new IED.

- ICT imports SCD file

  - ICT is able to import SCD file and create the instances of the IED in the ICT (SICS I21, I22)

- Final IED engineering as required

  - ICT uses the subscription information from SCT

    - Note: verification to be done by witness during test by observing what needs to be done in the IED tool by the engineer to create the binding of incoming external signals to internal signals (SICS I213, I42, I43)

- ICT configures the IED

  - IED can be configured

- ICT exports IID/XFactor file

  - ICT is able to produce IID/XFactor file with updated ExtRefs

- Check IID/XFactor file

  - Run IID/XFactor file through various SCL checkers and validators; report results for documentation

### Test case name: SUBMAINT-04

Description: Verify IED Behavior

Note: Steps D1 – D5 should be done for the newly added IED and for all existing IEDs that are receiving data from the new IED.

Test Steps:

- Verify step A5

  - Connect with a test client to the IED

- Verify step A9

  - Verify

- Verify step A8

  - Verify that reports are sent to the test client with the content as configured by the SCT (SICS I25 - I28)

- Verify step A9 Simulate GOOSE message

  - Verify	(SICS I25 – I28)

- Verify step A9 Simulate SV stream

  - Verify	(SICS I25 – I28)

### Test case name: SUBMAINT-05

Description: Update SCD file

Test Steps:

- SCT imports IID/XFactor files

  - SCT is able to import IID/XFactor files	(SICS S110)

- Update data flow based on updated ExtRefs

- Export updated SCD file

  - (SICS S61, S62)

### Test case name: SUBMAINT-06

Description: SCD file inspection

Test Steps:

- Verify step E2

  - In the SCD file, verify that the ExtRefs of the IEDs are updated based on what has been returned by the IID/XFactor files for IEDs

- Check SCD file

  - Run SCD file through various SCL checkers and validators; report results for documentation

## IED Replacement

### Test case name: SUBMAINT-07

Purpose:  Determine if a failed IED can be replaced by an unconfigured spare of the same type.

Preconditions and explanation: The test case begins with a fully functional IED which fails. It is assumed that a backup configuration of the IED is available. The “spare” IED is the same device as the “failed” IED except that it has a “factory default” configuration and the factory default IP address.
The test case continues with online loading of the configuration followed by verification that the configuration is now valid.

Preparation: Create a “backup configuration” as well as a “factory default configuration” for the IED. The incorrect configuration MUST have a different IP address than the IED is normally configured.

Test Steps:

- Verify the configuration version of the IED by polling <LDRoot>/LLN0.NamPlt.configRev. Record the configRev

- Reconfigure the IP address to factory default. If power cycling is needed, perform it in the next step.

- Disconnect power supply to IED, maybe wait 60 seconds to ensure GOOSE subscribers timeout?

- Restore power to the IED

- Use the ICT to inject the “factory default” configuration and verify that the IP address differs and NamPlt.configRev reports a different value than before.

- Use the ICT to inject the “backup configuration” into the IED

- Restore the IP address to the original value

- Verify that NamPlt.configRev reports the original value

# PTP

## Process bus clock failure Test Cases

Nominal set-up

The following test cases assume that there are (minimum) two PTP master clocks from two devices connected to the process bus. It shall be possible to disconnect them from the network without disconnecting other essential functions (e.g. a client IED) or there shall be a possibility to disable it.

### Basic Clock Test: PTP-NORM-01

This test is used to check that all IED are synchronized with the grandmaster Clock.

Requirements:

- All IEDs are fully configured and in operation.

- All master clock devices have been up and running for an enough time to ensure stabilization of the oscillator.

The test Description:

- Connect a client to the IED

- Read LTMS.TmSrc and LTMS.TmSyn (if available) on the IED under test.

LTMS.TmSrc Indicates GM ID use and LTMS.TmSyn shall indicate true

# IED Isolation Testing

Purpose:  To determine if IEDs can be tested as part of an integrated system.  There are two major use cases:

- The ability of an IED to operate of test unit data instead of real process data while still participating in the overall system. This allows IEDs to be provided test data and drive the whole system reaction based upon the test data.  This will be referred to as non-isolated testing/system testing.

- The ability of an IED to operate of test unit data instead of real process data and to be logically isolated from the rest of the system (e.g. the system knows not to use the information provided by the IED).  This will be referred to as isolated testing/unit testing.

The following table summarizes the test cases and if they are mandatory or optional for IED Isolation.

|  |  | m/o | Server/Publisher | Subscriber |
| --- | --- | --- | --- | --- |
| Normal execution in system | ISO-01 | m | x |  |
| Local/Remote Testing | ISO-02 | m | x |  |
| Test Mode | ISO-03 ISO-04 | m m | x | x |
| Test/Blocked Mode | ISO-05 ISO-06 | c1 m | x | x |
| Local Mode Lockout of Remote Controls | ISO-07 | m | x |  |

c1 – if IED supports Blocking.

c2- must support  LLN0.LocSta or LLN0.Loc or LLN0.LocKey.

Preconditions and explanation: In order to perform these tests, especially for GOOSE, dataSets must be created that include the appropriate quality values for the information being conveyed.  This is due to the fact that for use case 2, it will be the quality that conveys either the q.test = true.  It is this indication that other IEDs will need to use in order to determine if the data is usable for processing.  In order to be conformant, subscribing IEDs have to ignore data with q.test=true unless the subscribing IED is in test mode itself.

Please note that there are two bits for simulation/test: one in the GOOSE Ethernet reserved field, and one in the application level.

## Client/Server

### Precondition Test - Non-Isolated Testing/System Testing (IED mode “on”): ISO-01

Purpose:  This test is to ensure that an individual IED can utilize test set data and still participate in the overall system (i.e. the data sent by that IED has q.test=false).  This allows the system application to be tested using test sets.

Precondition:  The Server IEDs shall support LLN0.LocSta or LLN0.Loc or LLN0.LocKey.  If these DataObjects are not present, the witness shall make note and ISO-07 will not be able to be executed.

Precondition Verification:  IED is in mode “on” (Test Case 1)

### Test case name: ISO-02

Reason: To make sure that IEDs process the appropriate information as part of a normal maintenance process.

Precondition:  The IED under test must allow to switch Mod/Beh (must support  LLN0.LocSta or LLN0.Loc or LLN0.LocKey).  The IED must be in Remote.  The IED being tested has LLN0.Beh = “on”.

Test steps:

- The client will monitor the value of LLN0.Mod and LLN0.Beh.

- If the value is ON, no further action is required.  Otherwise, the client will set the value of Mod to ON.

Expected Results:  It is expected that the value of Mod.Beh will be ON.

### Test case name: ISO-03

Reason: To make sure that IEDs can set the test quality bit.

Precondition:  The IED under test must allow to switch Mod/Beh (must support  LLN0.LocSta or LLN0.Loc or LLN0.LocKey).  The IED must be in Remote.  The IED being tested has LLN0.Beh = “on”.

Test steps:

- The client will monitor the value of LLN0.Mod and LLN0.Beh.  The LLN0 shall be the highest in the Logical Device hierarchy.

- The client shall monitor if received

- The client will set LLN0.Mod = Test.

- The client will read a MX FCD that has quality and the witness shall check that the quality.Test = true.

If the LLN0 was not the highest in the hierarchy, then the MX FCD must be within the Logical Device for which the LLN0.Mod was set.

- The witness shall check that the qualities in published GOOSE/R-GOOSE messages have quality.Test = true.

- The witness shall check that the qualities in published SV/R-SV messages have quality.Test = true.

Expected Results:  It is expected the witness shall be able to observe that the client differentiates between process and test data.

### Test case name: ISO-04

Reason: To make sure that subscriber IEDs can process the test quality bit.

Precondition:  The IED under test must allow to switch Mod/Beh (must support  LLN0.LocSta or LLN0.Loc or LLN0.LocKey).  The IED must be in Remote.  The IED being tested has LLN0.Beh = “on”.

Test steps:

- The client will monitor the value of LLN0.Mod and LLN0.Beh.  The LLN0 shall be the highest in the Logical Device hierarchy.

- The client shall be placed into Test mode so that it can receive and process test data.

- The client will set LLN0.Mod = Test.

- The client will read a MX FCD that has quality and the witness shall check that the quality.Test = true.

If the LLN0 was not the highest in the hierarchy, then the MX FCD must be within the Logical Device for which the LLN0.Mod was set.

- The witness shall check that the qualities in published GOOSE/R-GOOSE messages have quality.Test = true.

- The witness shall check that the qualities in published SV/R-SV messages have quality.Test = true.

- The subscriber to GOOSE, R-GOOSE, SV, and R-SV should have LLN0.Beh = “on”.

- The witness should observe that the subscriber shall not process the data that has quality.test=true.

Expected Results:  It is expected that the value of Subscriber Mod.Beh will be “one”.  That the quality values provided by the server have the test bit=true. That the subscriber does not process the information that has the quality test bit set.

### Test case name: ISO-05

Reason: To make sure that IEDs can set the test quality bit test/blocked.

Precondition:  The IED under test must allow to switch Mod/Beh (must support  LLN0.LocSta or LLN0.Loc or LLN0.LocKey).  The IED must be in Remote.  The IED being tested has LLN0.Beh = “on”.

Test steps:

- The client will monitor the value of LLN0.Mod and LLN0.Beh.  The LLN0 shall be the highest in the Logical Device hierarchy.

- The client shall be placed into Test/Blocked mode so that it can receive and process test data.

- The client will set LLN0.Mod = Test.

- The client will read a MX FCD that has quality and the witness shall check that the quality.Test = true and quality.Test=Blocked are set.

If the LLN0 was not the highest in the hierarchy, then the MX FCD must be within the Logical Device for which the LLN0.Mod was set.

- The witness shall check that the qualities in published GOOSE/R-GOOSE messages have quality.Test = true and quality.Test=Blocked.

- The witness shall check that the qualities in published SV/R-SV messages have quality.Test = true and quality.Test=Blocked.

Expected Results:  It is expected that the value of Mod.Beh will be Test.  That the quality values provided by the server have the quality.Test bit=true and and quality.Test=Blocked

### Test case name: ISO-06

Reason: To make sure that subscriber IEDs can process the test and blocked quality bit.

Precondition:  The IED under test must allow to switch Mod/Beh (must support  LLN0.LocSta or LLN0.Loc or LLN0.LocKey).  The IED must be in Remote.  The IED being tested has LLN0.Beh = “on”.

Test steps:

- The LLN0 shall be the highest in the Logical Device hierarchy.

- The client will set LLN0.Mod = Test/Block.

- The client will read a MX FCD that has quality and the witness shall check that the quality.Test = true and quality.Blocked = true.

If the LLN0 was not the highest in the hierarchy, then the MX FCD must be within the Logical Device for which the LLN0.Mod was set.

- Need to attempt to operate a physical output of the IUT that is in test/blocked mode. Two options may be used:

  - Client Operates a control point that is tied to a physical output indicating operate.test attribute = true;

  - Publisher changes a GOOSE value that triggers an output.

Expected Results:  It is expected that the IUT shall not change the physical output.

### Test case name: ISO-07

Reason: To make sure that  IEDs can be placed into Local.

Precondition:  The IED under test must allow to switch Mod/Beh (must allow control i.e. LLN0.LocSta = false or LLN0.Loc=false or LLN0.LocKey=false).  The IED shall be in Remote. The IED being tested has LLN0.Beh = “on”.

Test steps:

- The client will monitor the value of .  The LLN0 shall be the highest in the Logical Device hierarchy.

- The IED shall be transitioned to Local mode through changing the values of . LLN0.LocSta,  LLN0.Loc,  or LLN0.LocKey. IED should be in Local.

The client will issue a control to the IED.

Expected Results:  It is expected that the control should fail.

### Test case name: ISO-08

Reason: To make sure that IEDs can set the test quality bit test/blocked and block outputs.

Precondition:  The IED under test must allow to switch Mod/Beh (must support  LLN0.LocSta or LLN0.Loc or LLN0.LocKey).  The IED must be in Remote.  The IED being tested has LLN0.Beh = “on”.

Test steps:

- The client will monitor the value of LLN0.Mod and LLN0.Beh.  The LLN0 shall be the highest in the Logical Device hierarchy.

- The client shall be placed into Test/Blocked mode so that it can receive and process test data.

- The client will set LLN0.Mod = Test.

- The client will read a MX FCD that has quality and the witness shall check that the quality.Test = true and quality.Test=Blocked are set.

If the LLN0 was not the highest in the hierarchy, then the MX FCD must be within the Logical Device for which the LLN0.Mod was set.

- The witness shall check that the qualities in published GOOSE/R-GOOSE messages have quality.Test = true and quality.Test=Blocked.

- The witness shall check that the qualities in published SV/R-SV messages have quality.Test = true and quality.Test=Blocked.

Expected Results:  It is expected that the value of Mod.Beh will be Test.  That the quality values provided by the server have the quality.Test bit=true and and quality.Test=Blocked

## GOOSE

### Test case name: ISO-08

Reason: To make sure that all IEDs which are currently not being tested ignore the simulated GOOSE.

Test steps:

- LPHD.Sim is set to false in the IED under test.

- Test set is configured to emulate all the GOOSE messages for which an IED subscribes for from a particular IED.

- Test set begins publishing the GOOSE messages with the Simulation bits set and data quality=good.

Expected Results:

- After step 3 it is expected that the IED under test will not take action on the test set information.

- If there is a monitoring substation HMI/Client (s), the instance of LGOS should be checked and normal operation of LGOS.NdsCom=false, LGOS.LastStNum should have good quality, LGOS.St shoud be True with good quality, LGOS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LGOS.SimSt should be false.

- The rest of the IEDs in the system should be not operate upon the information provided by the IED under test.

### Test case name: ISO-09

Reason: When an IED is switched to test mode it has to send all data with quality=test to inform the IEDs receiving (subscribing) data from this IED this data is the result from a test. This test case serves as a precondition for the following test case. If this test case fails, the following test case will also fail.

Precondition: The IED has to allow switching the behavior.

Test steps:

- The client switches the LD to test mode with a control sequence on LLN0.Mod and set it to test.

- The client switches the LD back to mode “on” with the same control sequence.

Expected results:

- After step 1 LLN0.Beh shows “test”.

- The GOOSE sent by this LD contain quality=test (but simulation=false)

- The clients receiving Reports from this LD will receive a Report with reason quality-change and the data contains quality=test.

- When a client reads data from this LD

  - all data in FC=ST in the LD will show up with quality=test.

  - all LNs in this LD show behavior “test” and the client is not able to change the behavior by changing Mod.

- If the IED has other LDs with a GrRef pointing to the LD in test mode

  - also these other LDs (and their LNs) have to show behavior “test” and the data in these LD has quality=test.

- GOOSE or Reports sent by other LDs which don’t have behavior=test must not have quality=test (note that other LDs may have a GrRef to the LD in test mode, thus they inherit the behavior from that LD).

- After step 2 LLN0.Beh shows “on” again.

- The GOOSE sent by this LD contain quality= good (and simulation=false)

- The clients receiving Reports from this LD will receive a Report with reason quality-change and the data contains quality=good.

- When a client reads data from this LD, all data in FC=ST in the LD will show up with quality= good.

### Test case name: ISO-10

Reason: An IED is currently being tested as part of a normal maintenance process. Other IEDs subscribe to GOOSEs from the IED under test and the HMI/SCADA receives Reports from the IED under test. The IEDs which subscribe to the IED under test (and the HMI/SCADA) thus have to ignore the data from the IED under test (marked with quality=test). Since the device is in test mode, process outputs are not blocked.

Precondition: The previous test case was passed (the LD in test mode correctly sends data with quality=test).

Test steps:

- The client switches the LD to test mode by changing LLN0.Mod of that LD.
An LD has to be used which is publishing a GOOSE that is subscribed by one of the other IEDs.

- The LPHD.Sim is set to true on the IED under test.

- Test set is configured to emulate all the GOOSE messages for which an IED subscribes for from a particular IED.

- The test set sends a GOOSE with simulated=true and data quality=normal.

- The test set changes a data value in the simulated GOOSE so that the IED under test will react with a data change.

  - If possible, this value change is accompanied by a process output change e.g., binary output.

Expected result:

- After step 1 the GOOSE sent by the LD in test mode contain quality=test (but simulation=false)

- It may be observable that the IEDs subscribing to this GOOSE ignore the data contained in this GOOSE (because their behavior is on).

- After step 5 the GOOSE sent by the LD in test mode shows a data change, but still with quality=test.

  - The test set may also recognize a process output change.

- The other IEDs don’t react on this data change.

### Test case name: ISO-11

Reason: An IED is currently being tested as part of a normal maintenance process. To avoid tripping the breaker during the test, the IED is set into mode “test-blocked”.

Precondition: The IED has behavior “normal”.

Test steps:

- The LPHD.Sim is set to true on the IED under test.

- Test set is configured to emulate all the GOOSE messages for which an IED subscribes for from a particular IED.

- The test set sends a GOOSE with simulated=true and data quality=normal.

- The test set changes a data value in the GOOSE so that a process output change (e.g. binary output change) is triggered on the IED under test.

- The IED under test is set to mode “test-blocked”.

- The test set changes a data value in the GOOSE so that a process output change would be triggered on the IED under test.

Expected result:

- After step 4, a process output change is observed by the test set.

- After step 5, the GOOSE sent by the IED under test contains quality=test and quality.operatorBlocked=TRUE

- After step 6, no process output shall happen. The status value of the process output shall not change.

## Sampled Values

Precondition:  LLN0.Mod should be set to set to a value of test/test-blocked.  All participating LNx.Mod value should be test/test-blocked.  The LLN0.Beh value should reflect a value of test/test-blocked (same with the LNx values).   This needs to be verified through HMI/Client interaction and represents a test case as part of the client/server part of this test.

### IED in test-blocked mode does not operate process output: ISO-12

Reason: An IED is currently being tested as part of a normal maintenance process. To avoid tripping the breaker during the test, the IED is set into mode “test-blocked”.

Precondition: The IED has behavior “normal”.

Test steps:

- The LPHD.Sim is set to true on the IED under test.

- Test set is configured to emulate all the SV streams for which an IED subscribes for from a particular IED.

- The test set sends the SV stream with simulated=true and data quality=normal.

- The test sends fault values in the SV stream so that the IED under test trips (i.e. a binary output is operated).

- The test sends nominal values in the SV stream so that the IED under test opens the trip contact.

- The IED under test is set to mode “test-blocked”.

- The test set sends fault values again, so that the IED would trip.

Expected result:

- After step 4, the protection trip is observed by the test set.

- After step 5, the test set sees that the trip contact is opened.

- After step 6, the GOOSE sent by the IED under test contains quality=test and quality.operatorBlocked=false

- After step 6

  - No change of the trip contact shall happen.

  - The test set and HMI/Client observes that the protection LN operated (PXXX.Op.general=true with quality=test).

Function with behavior off does not operate

### Test case name: ISO-13

Reason: An IED in operation contains functions out of service or they are switched off for testing purposes.

Precondition: The IED has behavior “normal”.

Test steps:

- The LPHD.Sim is set to true on the IED under test.

- Test set is configured to emulate all the SV streams for which an IED subscribes for from a particular IED.

- The test set sends the SV stream with simulated=true and data quality=normal.

- The test sends fault values in the SV stream so that the IED under test trips (i.e. a binary output is operated).

- The LN or LD with the function is set to mod=off.

- The test sends the same fault values in the SV stream so that the IED under test would trip (i.e. a binary output is operated).

- The test sends nominal values in the SV stream so that the IED under test trips.

Expected result:

- After step 4, the protection trip is observed by the test set.

- After step 5

  - No change of the trip contact shall happen.

# Disruptive Testing

## GOOSE

Precondition:  LLN0.Mod should be set to a value of ON.  All participating LNx.Mod value should be ON.  The LLN0.Beh value should reflect a value of ON (same with the LNx values).   This needs to be verified through HMI/Client interaction and represents a test case as part of the client/server part of this test.

### IED with LPHD.Sim=true get timeout if simulated GOOSE is missing: ABN-GOOSE-01

Reason: An IED with LPHD.Sim= true which received the simulated GOOSE once must not react on the not-simulated GOOSE anymore (note tissue 1151). This simulates the situation when the test set is removed after the test but somebody forgets to reset the Sim bit in the IED.

Test steps:

- LPHD.Sim is set to false in the IED under test.

- Test set is configured to emulate one of the GOOSE messages for which an IED subscribes for from a particular IED.

- Test set begins publishing one GOOSE message with Simulation bits set and data quality=good.

- The LPHD.Sim value is set to true in the IED under test.

- After some time, and observing the reaction of the IED under test, the test set is unplugged from the network.

- Restore LPHD.Sim to a value of false.

Expected Results:

- After step 3, it is expected that the IED under test will not take action on the test set information.
If there is a monitoring substation HMI/Client (s), the instance of LGOS should be checked and normal operation of LGOS.NdsCom=false, LGOS.LastStNum should have good quality, LGOS.St shoud be True with good quality, LGOS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LGOS.SimSt should be false.

- After step 4, It is expected that the IED under test will take action on the test set information.
If there is a monitoring substation HMI/Client (s), the instance of LGOS should be checked and normal operation of LGOS.NdsCom=false, LGOS.LastStNum should have good quality, LGOS.St shoud be True with good quality, LGOS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LGOS.SimSt should be true.

- After step 5, the IED under test will show a timeout.
If there is a monitoring substation HMI/Client (s), the instance of LGOS should be checked and the LGOS should indicate a timeout.

- After step 6, it is expected that the IED under test reacts on the normal GOOSE.
If there is a monitoring substation HMI/Client (s), the instance of LGOS should be checked and normal operation of LGOS.NdsCom=false, LGOS.LastStNum should have good quality, LGOS.St shoud be True with good quality, LGOS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LGOS.SimSt should be false.

### IED in on mode with LPHD.Sim=true ignores simulated GOOSE with data quality=test: ABN-GOOSE-02

Reason: An IED with behavior “on” must not process data with quality=test, regardless of the LPHD.Sim status.

Test steps:

- Test set is configured to emulate all the GOOSE messages for which an IED subscribes for from a particular IED.

- LPHD.Sim is set to true in the IED under test.

- Test set begins publishing the GOOSE messages with the Simulation bits set and quality=test.

- The test set changes values in the GOOSE message in an attempt to trigger a change in the receiving IED.

Expected results:

- After step 3 and 4 the receiving IED must not react on the simulated GOOSE.

## Sampled Values

Precondition:  LLN0.Mod should be set to a value of ON.  All participating LNx.Mod value should be ON.  The LLN0.Beh value should reflect a value of ON (same with the LNx values).   This needs to be verified through HMI/Client interaction and represents a test case as part of the client/server part of this test.

### IED with LPHD.Sim=true will get timeout if simulated SV is missing : ABN-SV-01

Reason:  An IED with LPHD.Sim=true which received the simulated SV once must not react on the not-simulated SV anymore (note tissue 1151). This simulates the situation when the test set is removed after the test but somebody forgets to reset the Sim bit in the IED.

Test steps:

- LPHD.Sim is set to false in the IED under test.

- Test set is configured to emulate all the SV messages for which an IED subscribes for from a particular IED.

- Test set begins publishing the SV messages with the Simulation bits set and data quality=good.

- The LPHD.Sim value is set to true in the IED under test.

- After some time, and observing the reaction of the IED under test, the test set is unplugged from the network.

- Restore LPHD.Sim to a value of false.

Expected Results:

- After step 3, it is expected that the IED under test will not take action on the test set information.
If there is a monitoring substation HMI/Client (s), the instance of LSVS should be checked and normal operation of LSVS.NdsCom=false,  LSVS.St shoud be True with good quality, LSVS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LSVS.SimSt should be false.

- After step 4, it is expected that the IED under test will take action on the test set information.
If there is a monitoring substation HMI/Client (s), the instance of LSVS should be checked and normal operation of LSVS.NdsCom=false, LSVS.St shoud be True with good quality, LSVS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LSVS.SimSt should be true.

- After step 5, the IED under test will get a timeout of the simulated SV stream.
If there is a monitoring substation HMI/Client (s), the instance of LSVS should be checked and it should indicate that the stream is not received anymore.

- After step 6, it is expected that the IED takes action on the normal SV stream.
If there is a monitoring substation HMI/Client (s), the instance of LSVS should be checked and normal operation of LSVS.NdsCom=false, LSVS.St shoud be True with good quality, LSVS.ConfRevNum’s value should equal the value in RxConfRevNum.  Additionally, LSVS.SimSt should be false.

## PTP

### Process bus clock failure Test Cases

Nominal set-up

The following test cases assume that there are (minimum) two PTP master clocks from two devices connected to the process bus. It shall be possible to disconnect them from the network without disconnecting other essential functions (e.g. a client IED) or there shall be a possibility to disable it.

#### Basic Clock Test: PTP-NORM-01

This test is used to check that all IED are synchronized with the grandmaster Clock.

Requirements:

- All IEDs are fully configured and in operation.

- All master clock devices have been up and running for an enough time to ensure stabilization of the oscillator.

The test Description:

- Connect a client to the IED

- Read LTMS.TmSrc and LTMS.TmSyn (if available) on the IED under test.

- LTMS.TmSrc Indicates GM ID use and LTMS.TmSyn shall indicate true

#### Antenna Lost Test: PTP-Disruptive-01

This test is used to check that all IED can seamless transfer between two GMC’s in synch.

Requirements:

- All IEDs are fully configured and in operation.

- All master clock devices have been up and running for an enough time to ensure stabilization of the oscillator.

- GMC’s connect to Process bus and Station Bus as redundant attached nodes (GMC’s see each other, only one active GMC)

The test Description:

- Disconnect Antenna on Active GMC (GMC #1)
Expected Results

- GMC #1 drops clock class from 7-> 6 and goes to passive

- GMC #2 goes to active

- MU and IED’s seamless transfer from GMC #1 to GMC #2

  - No jump in SmpCnt

  - SmpSynch remains Global

- No blocking protection functions
No false Trip or Start

  - MU’s and IED’s indicate Grandmaster Identity of GMC2 if supported
(SVStream / LTMS.TmSrc)

- Reconnect Antenna on Passive GMC (GMC1)
Expected Results

- GMC #1 increase clock class from 6-> 7 and goes to active

- GMC #2 goes to passive

- MU and IED’s seamless transfer from GMC #2 to GMC #1

- No jump in SmpCnt

- SmpSynch remains global

- No blocking protection functions
No false Trip or Start

- MU’s and IED’s indicate Grandmaster Identity of GMC #1 if supported
(SVStream / LTMS.TmSrc)

#### One of two GMC Lost Test: PTP-Disruptive-02

This test is used to check that all IED can handle local and global clocks and indicate correctly the current synchronization status. Protection IED’s are capable to distinguish between SV Streams subscribed that are local or global synched.

Requirements:

- All IEDs are fully configured and in operation.

- All master clock devices have been up and running for an enough time to ensure stabilization of the oscillator.

- GMC’s connect to Process bus and Station Bus as redundant nodes (GMC’s see each other, only one Active GMC)

The test Description:

- Power off Active GMC (GMC #1)
Expected Results

- GMC #2 goes to active

- MU and IED’s seamless transfer from GMC #1 to GMC #2

- No jump in SmpCnt

- SmpSynch remains Global

- No blocking protection functions
No false Trip or Start

- MU’s and IED’s indicate Grandmaster Identity of GMC #2 if supported
(SVStream / LTMS.TmSrc)

- Power on GMC (GMC #1)
Expected Results

- GMC #2 goes to passive

- GMC #1 goes active

- MU and IED’s seamless transfer from GMC #2 to GMC #1

- No jump in SmpCnt

- SmpSynch remains Global

- No blocking protection functions
No false Trip or Start

- MU’s and IED’s indicate Grandmaster Identity of GMC #1 if supported
(SVStream / LTMS.TmSrc)

#### Transition from Global to Local to Global: PTP-Disruptive-03

This test is used to check that all IED can seamless transfer between two GMC’s in synch.

Requirements:

- All IEDs are fully configured and in operation.

- All master clock devices have been up and running for an enough time to ensure stabilization of the oscillator.

- GMC’s connect to Process bus and Station Bus as redundant attached nodes (GMC see each other)

The test Description:

- Power off Active GMC’s (GMC #1 and GMX #2)
Expected Results

- MU’s and IED’s will select Best Master

- MU and IED’s seamless transfer from GMC to Best Local Master

- No jump in Smpcnt

- SmpSynch degrades from Global to Local (within hold over time)

- Protection functions depending on multiple sources might get blocked
No false Trip or Start

- ALL MU’s and IED’s indicate Grandmaster Identity of Best Master selected if supported (SVStream / LTMS.TmSrc)

- Power on GMC (GMC #2) before IED drift exceeds 4 us
Expected Results

- GMC #2 goes to active

- MU and IED’s seamless transfer from Local Best Master to GMC #2

- No jump in Smpcnt

- SmpSynch goes from Local to Global

- Protection functions depending on multiple sources get unblocked
No false Trip or Start

- MU’s and IED’s indicate Grandmaster Identity of GMC #2 if supported
(SVStream / LTMS.TmSrc)

- Repeat Step 2 Power off Active GMC (GMC2)
 Expected Results

- MU’s and IED’s will select Best Master

- MU and IED’s seamless transfer from GMC to Best Local Master

- No jump in Smpcnt

- SmpSynch degrades from Global to Local

- Protection functions depending on multiple sources might get blocked
No false Trip or Start

- ALL MU’s and IED’s indicate Grandmaster Identity of Best Master selected if supported (SVStream / LTMS.TmSrc)

- Power on GMC (GMC2) after IED drift exceeds 4 us
Expected Results

- GMC #2 goes to active

- MU and IED’s resynch and transfer from Local Best Master to GMC #2

- jump in SmpCtn

- SmpSynch goes finally to Global (drop to 0 might happen if hold over time exceeded)

- Protection functions depending on multiple sources get unblocked
No false Trip or Start

- MU’s and IED’s indicate Grandmaster Identity of GMC #2 if supported
(SVStream / LTMS.TmSrc)

- Power on GMC (GMC #1)

Expected Results

- GMC #1 goes to active

- GMC #2 goes passive

- MU and IED’s seamless transfer from GMC #2 to GMC #1

- No jump in SmpCnt

- SmpSynch remains Global

- No blocking protection functions
No false Trip or Start

- MU’s and IED’s indicate Grandmaster Identity of GMC2 if supported
(SVStream / LTMS.TmSrc)

#### Transition from Global to Local GMC Single Attached: PTP-Disruptive-04

This test is used to check that all IED can handle local and global clocks and indicate correctly the current synchronization status. 
Protection IED’s are capable to distinguish between SV Streams subscribed that are local or global synched.

Requirements:

- All IEDs are fully configured and in operation.

- All master clock devices have been up and running for an enough time to ensure stabilization of the oscillator.

- GMC’s connect to Station Bus as single attached nodes (GMC’s does not see each other, both GMC’s are active)

- The Process Bus is synchronized via Boundary Clocks.

The test Description:

- All IED’s synchronized to same GMC (GMC #1)
Expected Results

- MU’s and IED’s will select same GMC (e.g GMC #1)

- SmpSynch is Global

- Protection functions not blocked
No false Trip or Start

- ALL MU’s and IED’s indicate Grandmaster Identity of Best Master selected if supported (SVStream / LTMS.TmSrc)

- Power off Active GMC (GMC #1)
Expected Results

- MU and IED’s seamless transfer from GMC #1 to GMC #2

- No jump in SmpCnt

- SmpSynch remains Global

- No blocking protection functions
No false Trip or Start

- MU’s and IED’s indicate Grandmaster Identity of GMC #2 if supported
(SVStream / LTMS.TmSrc)

- Power off Active GMC’s (GMC #1 and GMX #2)
Expected Results

- MU’s and IED’s will select Best Master

- MU and IED’s seamless transfer from GMC #2 to Best Local Master

- No jump in SmpCnt

- SmpSynch degrades from Global to Local

- Protection functions depending on multiple sources might get blocked
No false Trip or Start

- ALL MU’s and IED’s indicate Grandmaster Identity of Best Master selected if supported (SVStream / LTMS.TmSrc)

- Power on all GMC’s before IED drift exceeds 4 us 
Expected Results

- MU’s and IED’s will select same GMC (e.g GMC #1)

- MU and IED’s seamless transfer from Local Best Master to Global Best Master (e.g. GMC #1)

  - No jump in Smpcnt

  - SmpSynch is Global

- Protection functions not blocked
No false Trip or Start

  - ALL MU’s and IED’s indicate Grandmaster Identity of Best Master selected if supported (SVStream / LTMS.TmSrc)

#### System Robustness: PTP-Disruptive-05

This test is used to check behavior of all IED’s and MU’s in case of disruptive GMC connection.

Requirements:

- All IEDs are fully configured and in operation.

- All master clock devices have been up and running for an enough time to ensure stabilization of the oscillator.

- GMC’s connect to Station Bus as single attached nodes (GMC’s does not see each other, both GMC’s are active)

- The Process Bus is synchronized via Boundary Clocks.

The test Description:

- All IED’s synchronized to same GMC (GMC #2)

  - Identify the port on the switch where the GPS clock PTP message in coming

  - Remove and replace Fiber a number of times in quick succession (faster than 3 seconds).

Expected Results

- No effect Time synchronisation is maintained

- No jump in SmpCnt

- SmpSynch remains Global

- No blocking protection functions
No false Trip or Start

- MU’s and IED’s indicate Grandmaster Identity of GMC2 if supported
(SVStream / LTMS.TmSrc)

## IED Failure/Power Down

### Client/Server

#### IED Failure / Power down Testing: ABN-IEDFAIL-01

Purpose:  To determine if an IED disconnect from /reconnect to an integrated system is detected.  There are two major use cases:

1.	IED A is integrated as a GOOSE publisher.  As such, it publishes at least one GOOSE message and at least one other IED B subscribes to this GOOSE.

2.	IED A is integrated as a server to provide integrity reports.  At least one client is associated with this server and enabled the report in the server IED A.

Preconditions and explanation:  Under idle condition, i.e. without state changes (value, quality) of events which are configured for transmission,

IED A issues

- GOOSE message(s) at the maximum time interval(s) of re-transmission

- integrity report(s) at the time interval(s) set by the individual client(s)

- ‘TCP Keep alive’ messages at a time interval specified for the IED communication unit

- ‘TCP Keep alive’ responses to the ‘TCP Keep alive’ request(s) of the client(s)

The client issues

- ‘TCP Keep alive’ messages at a time interval specified for the client communication unit

- ‘TCP Keep alive’ responses to the ‘TCP Keep alive’ request of IED A

For this test case, ‘IED failure’ is understood as an impact to the device which completely disables its ability to communicate, similar to at a power loss.  It is not assumed that an IED delivers self-supervision signals or indications of a degraded mode before ceasing communications.  Also, it is of no relevance whether or not the IED saves communication related data to a non-volatile memory upon the detection of a failure/power down.

#### Test case name: ABN-IEDFAIL-02

After the expiration of ‘TCP Keep alive’, the client supervision shall detect a communication loss.

Test description:

| A1 | Power down IED A |
| --- | --- |
| R1a | (using a protocol analyser) - no more integrity reports from IED A - ‘TCP Keep alive’ messages from the client - no more ‘TCP Keep alive’ responses from IED A - no more ‘TCP Keep alive’ messages from the IED - no more ‘TCP Keep alive’ responses from the client |
| R1a | (if provided by the client) indication of the loss of communication with IED A |

#### Testing IED restart / power up of a report server: ABN-IEDFAIL-03

Purpose:  This test is to ensure that after an server IED restart reporting is re-established.

Precondition:

1.	IED A is configured with a report control block, an associated data set including at least one data object.

2.	The client is configured to consume the IED A report.

3.	IED A is powered down.

Precondition Verification:

•	Results as per TC IEDfailReport-1

#### Test case name: ABN-IEDFAIL-04

Test description:

| A1 | Power up IED A, wait for restart completed |
| --- | --- |
| R1a | (using a protocol analyser) - ‘TCP Keep alive’ messages from the client - ‘TCP Keep alive’ responses from IED A - ‘TCP Keep alive’ messages from IED A - ‘TCP Keep alive’ responses from the client |
| R1b | (using a protocol analyser) - [The client establishes an association with IED A] - The client writes to the report control block in IED A (OptFlds, TrgOps [integrity, IntgPd], RptEna) |
| R1c | (using a protocol analyser) The client issues a GI command for the report |
| R1d | (using a protocol analyser) IED A issues a report |
| R1e | (using a protocol analyser) integrity reports from IED A |

Remarks:

No test of client reservation, since the secure client identification is not yet standardized.

No test of resynchronization to the last proper report (in case of buffered reporting), since after the restart of an faulty/powered down IED the report buffer does not contain the elements sent earlier any longer.

### GOOSE

#### Testing the GOOSE publisher IED failure / power down: ABN-IEDFAIL-05

Purpose:  This test is to ensure that losing the GOOSE message stream from IED A is detected by the subscribing IED B.

Precondition:

      - IED A is configured with a GOOSE control block, an associated data set including at least one pair of stVal/q data attributes.  GOOSE publishing is enabled.

IED B is configured to subscribe the IED A GOOSE data.

Precondition Verification:

- (using a protocol analyser) IED A publishes GOOSE messages

- (using a protocol analyser) The sequence numbers SqNum of the published GOOSE messages increment with each GOOSE message.

- If there is a monitoring substation HMI/Client(s) connected to IED B, the instance of LGOS is checked for

      - LGOS.NdsCom=False

      - LGOS.LastStNum=[don’t care], good quality

      - LGOS.St=True, good quality

      - LGOS.ConfRevNum=RxConfRevNum

      - LGOS.SimSt=False (no simulation testing here)

#### Test case name: ABN-IEDFAIL-06

After the expiration of the TAL, the IED B GOOSE supervision shall signal a communication loss.

Test description:

| A1 | Power down IED A |
| --- | --- |
| R1 | (using a protocol analyser) no more GOOSE messages from IED A |
| A2 | Wait for a time longer than 2 x TAL |
| R2 | IED B LGOS instance: LGOS.St=False, good quality |

#### Testing IED restart / power up of a GOOSE publisher: ABN-IEDFAIL-07

Purpose:  This test is to ensure that after an IED restart GOOSE publishing is recommenced and GOOSE subscription is re-established.

Precondition:

1.	IED A is configured with a GOOSE control block, an associated data set including at least one pair of stVal/q data attributes.  GOOSE publishing is enabled.

2.	IED B is configured to subscribe the IED A GOOSE data.

3.	IED A is powered down.

Precondition Verification:

•	Results as per TC IEDfailGOOSE-1

#### Test case name: ABN-IEDFAIL-08

After the restart of IED A, IED A resumes GOOSE publishing, IED B GOOSE supervision indicates a trustful communication.

Test description:

| A1 | Power up IED A, wait for restart completed |
| --- | --- |
| R1a | (using a protocol analyser) IED A publishes GOOSE messages |
| R1b | IED B LGOS instance: LGOS.St=True, good quality |

Testing IED restart / power up of a GOOSE subscriber

Purpose:  This test is to ensure that after an subscribing IED restart GOOSE subscription is re-established.

Precondition:

1.	IED A is configured with a GOOSE control block, an associated data set including at least one pair of stVal/q data attributes.  GOOSE publishing is enabled.

2.	IED B is configured to subscribe the IED A GOOSE data.

3.	IED B is powered down.

Precondition Verification:

•	(using a protocol analyser) IED A publishes GOOSE messages

•	(using a protocol analyser) The sequence numbers SqNum of the published GOOSE messages increment with each GOOSE message.

•	If there is a monitoring substation HMI/Client(s), IED B cannot be reached.

#### Test case name: ABN-IEDFAIL-09

After the restart of IED B, IED B GOOSE supervision indicates a trustful communication.

Test description:

| A1 | Power up IED B, wait for restart completed |
| --- | --- |
| R1 | IED B LGOS instance: LGOS.St=True, good quality |

Testing the server IED failure / power down impact on Reporting

Purpose:  This test is to ensure that losing the reporting from server IED A is detected by the client.

Precondition:

1.	IED A is configured with a report control block, an associated data set including at least one data object.

2.	The client is configured to consume the IED A report.

3.	The client established an association with IED A

4.	The client wrote to the report control block in IED A

- OptFlds

- TrgOps [integrity, IntgPd]

- RptEna

Precondition Verification:

- (using a protocol analyser) IED A issues reports at the time interval set by the client

- (using a protocol analyser) ‘TCP Keep alive’ messages from the client

- (using a protocol analyser) ‘TCP Keep alive’ responses from the IED

- (using a protocol analyser) ‘TCP Keep alive’ messages from the IED

- (using a protocol analyser) ‘TCP Keep alive’ responses from the client

### Merging Unit Failure

Stand Alone Merging Unit (SAMU) will typically have functions to indicate the operational status of the device. The indications can be visual by the use of LEDS, mechanical by the use of contacts, and electronically by the use of a graphical user interface and/or inherent indications in the IEC 61850-9-2 sampled value protocol or IEC 61850 GOOSE messaging.

A typical setup with the use of contacts to indicate the operational status of a SAMU is shown in the figure below.

Operational status of whether or not the SMAU is In Service, GPS time synchronization, internal alarm, and system failure are typical.

The SAMU may have a configuration interface that provides the device health to an operator with access to the device. The front panel of a SAMU may have LEDs to visually indicate the health of the device.

A brief summary of a typical SAMU indication of health is as follows:

Equipment Healthy: Shows the device health, which is classified as follow:

- OK: Device is totally functional, no alarms reported. IN SERVICE LED: ON; ALARM LED: OFF; IN SERVICE RELAY: OPEN.

- WARNING: The device is functional, but has alarms reported. IN SERVICE LED: ON; ALARM LED: ON; IN SERVICE RELAY: OPEN.

- ALARM: The device is not functional. IN SERVICE LED: OFF; ALARM LED: ON; IN SERVICE RELAY: CLOSED

#### USES CASES

##### Hardware Failure

The internal watchdog functions of a SAMU are not accessible and do not have access points that would allow testing of these function. Disrupting the power supply to the SAMU during normal operation would simulate failure of the SAMU and cause the device to become non-operational.

##### Time Synchronization Failure

The synchronization algorithm in a SAMU maybe quite different between SAMU, but there should be a common function amongst SAMU from different manufacturers.  This function is the “Holdover Time” that occurs after the time sync signal is not detected by the SAMU. The SAMU is designed to provide accurate operation during the “Holdover Time” duration, the duration will be different amongst SMAU manufacturers.

##### Quality Bit Indications (Out of Range, Failure etc…)

The SV telegram will contain information about the quality of the data contained in the telegram. The SAMU will have a default setting for the various bits in the quality field, the default setting may also be changed by the SAMU. There may be an option to change certain quality bits for test purposes.

#### TEST CASES

##### Hardware Failure: MERG-FAIL-01

Precondition:

The SAMU is operating under normal conditions

Test Step:

Disrupt power to the SAMU

Expected Results:

The IN-SERVICE contact should change to indicate failure. The contact should be a NC contact such that it is closed during failure.

##### Time Synchronization Failure: MERG-FAIL-02

Precondition:

The SMAU is operating under normal conditions

Test Step:

- Disconnect the time source signal to the SAMU

- The SAMU “Holdover Time” duration will start timing.  The SV telegrams still indicate that the SMAU is synchronized

- When the SMAU “Holdover Time” duration has expired the SMAU will enter into a free running mode

- The Synchronization contact and/or LED should indicate failure of the time synchronization

- The SV telegrams should indicate the unsynchronized condition within the telegram

- Reconnect the time source signal to the SAMU

Expected Results:

- The SAMU will enter into a process of resynchronization and this process will be dependant on the manufacturer’s implementation

- The SMAU should enter into a new state of normal operation with all alarms and indications reset.

##### Quality Bit Indications (Out of Range, Failure etc…)

The test conditions necessary to create the scenarios where the quality bits will be changed by the SMAU are difficult to produce and potentially dangerous due to the magnitudes of the input signals required. The SMAU may have an interface whereby the various quality bits can be set by the user for test purposes.  The SMAU user manual should be consulted for the manufacturer specific cases necessary to operate the quality bits.

Bits 2, 4, 5, 7, 8, 12 should always be set to False as compliant to IEC 6189-9

###### Test case name: MERG-FAIL-03

Precondition:

The SMAU is operating under normal conditions

Test Step:

- Set the Out of Range Quality bit 2 to True

- The Validity bits 1:0 should indicate invalid

Expected Results:

Check the SV telegram

###### Test case name: MERG-FAIL-04

Precondition:

The SMAU is operating under normal conditions

Test Step:

Set the Failure Quality bit 6 to True

Expected Results:

Check the SV telegram

###### Test case name: MERG-FAIL-05

Precondition:

The SMAU is operating under normal conditions

Test Step:

Set the Inaccurate Quality bit 9 to True

Expected Results:

Check the SV telegram

###### Test case name: MERG-FAIL-06

Precondition:

The SMAU is operating under normal conditions

Test Step:

Set the Test Quality bit 11 to True

Expected Results:

Check the SV telegram

## EAP failure

Purpose:  This suite of testing is to determine the reaction to failures of the EAP Firewall function.  In general, there are two types of firewalls that need to be tested and the expected behavior is different based upon the type of firewall.  The known types of firewalls, for the purposes of this testing are:

- Firewalls with failsafe/pass-through capability.

In this particular instance, if a firewall fails or has power removed, Ethernet traffic is not interrupted.  In this mode, no access control, deep packet inspection, or other firewall/EAP functions would be expected.

- Firewalls implemented as a redundant/failover pair.

In this particular instance, if a firewall fails or has been power removed, the “standby” firewall will begin processing information within a specific period of time.

- Firewalls with no-failsafe/pass-through capability.

In this particular instance, if a firewall fails, or has power removed, communication is expected to be interrupted.

In either event, monitoring of the firewall itself needs to provide an indication of the failure of the firewall.

### Firewall with Failsafe Testing

#### Test case Name:  EAP-PDF-01

Precondition:  Firewall is operational.  All client/server and GOOSE communication should be operational and validated.    Firewall needs to document the failsafe time.

Test Step:  Remove power from Firewall

Expected Results:

Client/Server:  No interruption of communication

GOOSE:  No TAL expirations should be detected except < failsafe time.

Monitoring of firewall: monitoring should indicate that firewall is failed

#### Test case Name:  EAP-PD-REC-02

Precondition: Firewall is powered-down.  All client/server and GOOSE communication should be operational and validated.    Firewall must document the power-up time.

Test Step:  Power-up the Firewall

Expected Results:

Client/Server:  No interruption of communication

GOOSE:  No TAL expirations should be detected except < power-up time

Monitoring of firewall: After power-up time, monitoring should indicate that firewall is operational.

## Redundant Firewall

#### Test case Name:  EAP-RED-PDF-01

Precondition: Both primary and secondary  Firewalls are operational.  All client/server and GOOSE communication should be operational and validated.    Firewall needs to document the failsafe time.

Test Step:  Remove power from Primary Firewall

Expected Results:

Client/Server:  No interruption of communication

GOOSE:  TAL expirations may occur and should be documented as the redundancy is not bumpless due to source MAC changes < failsafe time.  Subscribers that “bump” should be documented.

Monitoring of firewall:  Should indicate that Primary Firewall is failed and that the Standby firewall is active and operational.

#### Recovery from failure: EAP-RED-PDF-02

Precondition: Primary Firewall is powered-down.  All client/server and GOOSE communication should be operational and validated.    Firewall needs to document the power-up time.

Test Step:  Power-up the Primary Firewall

Expected Results:

Client/Server:  No interruption of communication

GOOSE:  No TAL expirations should be detected except.

Monitoring of firewall:  Should indicate that the primary firewall is operational and that the secondary firewall is operational and active.

## Firewall with no failsafe

### Test case Name:  EAP-NOSAFE-PDF-01

Precondition:  Firewall is operational.  All client/server and GOOSE communication should be operational and validated.    Firewall needs to document the failsafe time.

Test Step:  Remove power from Firewall

Expected Results:

Client/Server:  Clients should provide an indication that the connections have been interrupted within 1 minute.

GOOSE:  TAL expirations should be  detected within 1 minute.

Monitoring of firewall: monitoring should indicate that firewall is failed

### Recovery from failure: EAP-NOSAFE-PDF-02

Precondition: Firewall is powered-down.   All client/server and GOOSE communication should be failed.    Firewall needs to document the power-up time.

Test Step:  Power-up the Firewall

Expected Results:

Client/Server:  Communication should be re-established within 1 minute of completion of power-up.

GOOSE:  GOOSE should be received within 1 minute of power-up.

Monitoring of firewall: After power-up time, monitoring should indicate that firewall is operational.

# Firewall/EAP and GOOSE Monitoring Testing

## Use case: Intruder with different source MAC address and power-up

### Test case name: GOOSE-SEC-INT-01

Precondition:  Subscriber(s) are subscribed to the expected publisher and the publisher is publishing and there are no TAL expirations occurring.

Test Step:  The intruding publisher is configured to publish the expected GOOSE but from a different source MAC address from the expected publisher.  Additionally, the Stnum shall be starting at 0 indicating power-up and a set of constant values so that observation in regards to which GOOSE is being used is facilitated.

Expected Results:

The EAP/Firewall and monitors should detect the intruder.  EAP/Firewalls should use ACL to prevent the GOOSE through flowing through the EAP.

## Use Case: Intruder with the same source MAC address and power-up

### Test case name: GOOSE-SEC-INT-02

Precondition:  Subscriber(s) are subscribed to the expected publisher and the publisher is publishing and there are no TAL expirations occurring.

Test Step:  The intruding publisher is configured to publish the expected GOOSE but from and the same source MAC address from the expected publisher.  Additionally, the Stnum shall be starting at 0 indicating power-up and a set of constant values so that observation in regards to which GOOSE is being used is facilitated.

Expected Results:

The EAP/Firewall and monitors should detect the intruder due to multiple different StNums.  EAP/Firewalls should use ACL to prevent the GOOSE through flowing through the EAP.

## Use Case: Intruder with the same source MAC address and future StNum

### Test case name: GOOSE-SEC-INT-03

Precondition:  Subscriber(s) are subscribed to the expected publisher and the publisher is publishing and there are no TAL expirations occurring.

Test Step:  The intruding publisher is configured to publish the expected GOOSE but from and the same source MAC address from the expected publisher.  Additionally, the Stnum shall be starting at a large number and a set of constant values so that observation in regards to which GOOSE is being used is facilitated.

Expected Results:

The EAP/Firewall and monitors should detect the intruder due to multiple different StNums.  EAP/Firewalls should use ACL to prevent the GOOSE through flowing through the EAP.

# Network Failure

## Test case name: NET-FAIL-01

Purpose:  Verify that devices on both ends of the connection-oriented association recover from a network failure.

Precondition:  Intact network with the client associated with the server.

Narrative: The network usually consists of a server, at least one intervening Ethernet switches, and a client. Sometimes an IED can detect loss of the physical link but often this detection is based upon lack of TCP keep-alives. Thus test verifies the 8 cases of client/server and physical-link-loss-detection yes/no.
The 60 second delay before network restoration simulates a long-term failure, 2 seconds a short-term failure.

### Test case 1a: Short/Long disconnection at the server switch

Test Steps 1a:

- Remove the connection between the server/PC/switch and the remainder of the network.

- Wait for 2 seconds

- Re-attach the network

- Verify that the client has restored the connection to the server within 60 seconds

- Remove the connection between the server/PC/switch and the remainder of the network.

- Wait for more than 60 seconds (or less if both sides acknowledge loss of connection)

- Re-attach the network

- Verify that the client has restored the connection to the server within 60 seconds

### Test case 1b: Short/Long disconnection at the server

Test Steps 1b:

- Remove the connection at the server

- Wait for 2 seconds

- Re-attach the network

- Verify that the client has restored the connection to the server within 60 seconds

- Remove the connection at the server

- Wait for more than 60 seconds (or less if both sides acknowledge loss of connection)

- Re-attach the network

- Verify that the client has restored the connection to the server within 60 seconds

## Test case name: NET-FAIL-02

### Test case 2a: Short/Long disconnection at the client switch

Test Steps 2a:

- Remove the connection between the client /PC/switch and the remainder of the network.

- Wait for 2 seconds

- Re-attach the network

- Verify that the client has restored the connection to the server within 60 seconds

- Remove the connection between the client /PC/switch and the remainder of the network.

- Wait for more than 60 seconds (or less if both sides acknowledge loss of connection)

- Re-attach the network

- Verify that the client has restored the connection to the server within 60 seconds

### Test case 2b: Short/Long disconnection at the client

Test Steps 2b:

- Remove the connection at the client

- Wait for 2 seconds

- Re-attach the network

- Verify that the client has restored the connection to the server within 60 seconds

- Remove the connection at the client

- Wait for more than 60 seconds (or less if both sides acknowledge loss of connection)

- Re-attach the network

- Verify that the client has restored the connection to the server within 60 seconds

Annex A (Informative)

# Validation of device synchronization (used by most clock synchronization tests)

The following procedure explains how time synchronization of each device, will be validated on the application level.

Depending on the device under test, different methodologies could be used to validate time synchronization.  In all case, this will be done using a synchronized simulation signal which is synchronized to the time server and then by retrieving timestamped process data triggered by this simulated signal.

The simulated signal could be of different types: Digital IOs, Analog (i.e.  synchrophasor simulation, time synchronized fault event), integer (counter), GOOSE(software simulated), etc.

The following diagram shows how synchronized signals could be generated from externally synchronized signal simulators:

The easiest way to produce timestamped data is probably using a synchronized toggling digital signal.  Most of the devices under tests support digital inputs.  Simply by publishing the status of the digital input using GOOSE or MMS, it will be possible to monitor the timestamp of this digital point.  A simple PPS signal (1Hz) is sufficient to easily verify the synchronization.

In order to simplify the analysis of the resulting application values, the monitoring system collecting the application level values shall also be synchronized.  This way, it is quite easy to make sure that timestamps are marked with the correct second.  (This requirement can be a bit tricky when testing leap seconds, since windows systems doesn’t nicely handle leap second.  For those tests, the monitoring system clock synchronization can be first synchronized, then disabled in order to collect sequential data during the leap second.)

Using the a digital signal, the validation is done as follow:

- Validate that the rising edge of the digital signal occurs on the top of the second.

  - For GOOSE check the timestamp of the value in the message when stVal change to true.

  - For MMS, check the timestamp of the value in the reports when stVal change to true.

- Validate that the time (second) of the timestamp is matching the time of the monitoring system.

- Validate time quality

  - Quality bits should match expected test result: LeapSecondKnown (LSK), ClockNotSynchronized (CNS), ClockFailure (CF)

  - In all cases, the difference between the observed timestamp and the simulation shall be within the uncertainty defined by the (timestamp time quality + simulation uncertainty).

(The falling edge of the signal can also be used; it should match the duty cycle of the simulation signal.)